# GL-012 STEAMQUAL
Steam Quality Controller
Implementation Playbook

Consolidated into GL-003 UNIFIEDSTEAM

Version 1.0 | December 23, 2025

Audience: AI/ML, Data Engineering, Software Development, Controls/Automation, Mechanical/Thermal, Electrical/Instrumentation, Climate Intelligence, Cybersecurity, QA/Testing, Program Management

Important: GL-012 is not shipped as a standalone agent. Its scope is implemented as the Steam Quality domain module inside GL-003 UNIFIEDSTEAM. This document defines the work package, interfaces, and acceptance criteria for that module.

# Document Control

This playbook is the single source of truth for implementing the Steam Quality domain module (formerly GL-012 STEAMQUAL) within GL-003 UNIFIEDSTEAM.

| Field | Value | Field | Value |
| --- | --- | --- | --- |
| Agent ID | GL-012 (consolidated into GL-003) | Module Name | SteamQualityController |
| Short Code | STEAMQUAL | Domain | Steam Systems |
| Priority | Low (P2) | Target Release | Q2 2026 |
| Approvals | Program Steering Committee / Plant Ops | Status | Draft for execution |

# 1. Executive Summary

GL-012 STEAMQUAL was originally conceived as a dedicated controller for steam quality (moisture separation, dryness fraction estimation, and steam quality monitoring). The scope is now consolidated into GL-003 UNIFIEDSTEAM as a domain module that provides:

Real-time estimation of steam dryness fraction and moisture carryover risk (soft sensing plus validation instrumentation).

Closed-loop and supervisory control recommendations that keep steam within quality limits while minimizing energy penalty and equipment wear.

Quality event detection, root-cause analytics, and operator guidance integrated into the unified steam optimizer.

Measurement governance: sensor selection, calibration workflows, data quality, and uncertainty reporting for quality metrics.

This document tells each team what to build, what data is required, how the thermodynamics and mathematics work, what integration points are needed inside GL-003, and how we will test and accept the Steam Quality module.

# 2. Scope and Non-Scope

## 2.1 In Scope

Steam quality monitoring at key headers and consumers (turbines, process heaters, sterilizers, evaporators, etc.).

Dryness fraction (quality) estimation for saturated/wet steam, and carryover detection risk scoring for superheated steam.

Moisture separation system monitoring and control: separators, scrubbers, steam traps, drains, reheaters/dryers (where present).

Alarms and advisories: low dryness, high moisture, carryover risk, separator flooding, trap failure, water hammer risk.

Data products for GL-003: quality KPIs, predicted quality trajectories, recommended actions, and constraint limits for optimization.

Model validation against reference instrumentation (calorimeters, optical moisture meters, lab sampling) where available.

## 2.2 Out of Scope

Standalone deployment as an independent agent (all deployment is via GL-003).

Boiler combustion optimization and feedwater chemistry optimization beyond quality monitoring interfaces (handled by other GL-00x modules).

Detailed design or replacement of mechanical separator hardware (engineering recommendations only).

Safety instrumented system (SIS) logic changes without an approved safety lifecycle (the module may recommend but not override SIS).

# 3. Key Concepts and Definitions

Steam quality is a multi-dimensional concept. For this module, we track at minimum the following quality dimensions:

| Metric | Symbol | Definition | Why it matters |
| --- | --- | --- | --- |
| Dryness fraction | x | Mass fraction of vapor in a saturated liquid-vapor mixture (0 to 1). Moisture mass fraction = 1 - x. | Low x increases erosion, reduces heat transfer performance, and can cause water hammer. |
| Moisture carryover risk | R_carry | Probability or score that liquid droplets are being entrained and transported downstream, including under superheated conditions. | Carryover damages turbines/valves, contaminates process, and creates transient shocks. |
| Superheat margin | DeltaT_sh | T - T_sat(P). Positive margin indicates superheated steam. | Low margin increases condensation risk during pressure drops or heat losses. |
| Contamination (solids) | TDS, SiO2, Na | Concentration of dissolved/entrained solids and silica/sodium indicators in steam/condensate. | Contamination causes deposits, corrosion, and turbine blade fouling. |
| Separator performance | eta_sep | Moisture removal efficiency of separator/scrubber based on inlet/outlet moisture estimates. | Degraded performance drives quality loss and increases drain system load. |
| Condensate quality | Cond, pH, DO | Conductivity, pH, dissolved oxygen in condensate return. | Signals carryover/contamination and informs water chemistry and corrosion control. |

Terminology notes:

For superheated steam, dryness fraction x is effectively 1.0; however, droplet entrainment can still occur. The module therefore uses both x (when applicable) and carryover risk scoring.

Dryness fraction is defined at thermodynamic equilibrium. In real piping, droplets may be non-equilibrium; instrumentation and estimation must account for this.

# 4. Objectives and KPIs

The Steam Quality module must drive measurable improvement in reliability, efficiency, and safety. KPIs are reported by header, unit, and shift/day.

| KPI | Target / Guideline | Computation | Owner | Acceptance Criteria |
| --- | --- | --- | --- | --- |
| Steam dryness fraction at critical headers | >= 0.98 (turbine headers), >= 0.95 (process, configurable) | x_est (soft sensor) validated by reference measurements; report min/avg | Ops + Controls | Bias < 0.01 vs reference for validated periods; availability > 99% |
| Carryover events | Trend to zero; severity-classified | Count of quality excursions beyond limits, with duration and severity | Ops | Detection latency < 60 s for sensor-based events; < 5 min for analyzer-based |
| Separator flooding / trap failure rate | Continuous improvement | MTBF and alarms per month, correlated with maintenance | Maintenance | Precision > 80% for known failures (post-mortem labeling) |
| Energy penalty from quality controls | Minimize | Incremental fuel/steam cost from drain/reheat actions | Engineering | Optimization keeps cost impact within constraints while meeting quality |
| Water hammer risk score | Low | Derived from pressure transients, condensate pooling indicators | Safety/Controls | False negative rate < agreed threshold; always fail-safe (alert) |
| Model drift | Stable | Rolling error and data drift metrics | AI/ML | Automatic alerts when drift exceeds threshold; rollback supported |
| Carbon intensity impact | Report and reduce | CO2e saved from reduced losses and improved efficiency | Climate Intelligence | Methodology documented; auditable inputs |
| Operator trust | High | User feedback score on advisories and alarms | Product/Ops Excellence | >= agreed satisfaction benchmark in pilot |

All targets are site-specific and must be parameterized. This module must support configuration per plant, header, and consumer class.

# 5. System Context (Where Steam Quality Is Controlled)

Steam quality is influenced by generation, separation/drying, distribution, and end-use conditions. The module must model and monitor the full path from boiler outlet to critical consumers.

## 5.1 Typical steam quality control points

Boiler drum and steam drum separation (carryover risk increases with high drum level, foaming, high load swings).

Superheater and attemperator/desuperheater (superheat margin management).

Moisture separator / steam scrubber (mechanical separation, drain handling).

Steam traps and drip legs (condensate removal, pooling prevention).

Pressure reducing valves (PRVs) and control valves (Joule-Thomson and throttling effects may induce condensation).

Distribution losses (heat loss, insulation condition, ambient conditions).

Consumers: turbines (erosion), heat exchangers (heat transfer reduction), sterilizers (process quality), etc.

## 5.2 Conceptual architecture (physical)

Boiler/Drum -> Superheater -> (Optional) Attemperator -> Separator/Scrubber -> Main Header -> PRVs/Valves -> Branch Headers -> Consumers
                              |                       |                 |              |              |
                              |                       +-> Drains/Traps <-+              +-> Condensate return
                              +-> Blowdown/chemistry monitoring

The module must support multi-header plants and multiple steam pressure levels (HP/MP/LP).

# 6. Functional Requirements

Functional requirements are stated in implementable terms for GL-003 integration.

| ID | Requirement | Inputs/Dependencies | Acceptance Criteria |
| --- | --- | --- | --- |
| FR-01 | Ingest steam quality related tags from OT systems and historians with timestamp alignment and unit normalization. | OPC-UA/Modbus/PI/Historians; time sync; tag dictionary | >= 99% data availability for critical tags; unit tests for conversions |
| FR-02 | Compute real-time superheat margin and saturation state using steam tables. | Pressure, temperature; steam property library | Errors < 0.5 C for DeltaT_sh vs reference property calc |
| FR-03 | Estimate dryness fraction x for saturated/wet steam with uncertainty bounds. | Calorimeter data (if any), P/T/flow; hybrid model | Bias < 0.01 vs reference during validation; provide 95% CI |
| FR-04 | Produce carryover risk score R_carry for all headers, including superheated steam. | P/T transients, drum level, separator DP, condensate conductivity, etc. | Detect known carryover incidents with recall >= 85% in pilot dataset |
| FR-05 | Detect separator flooding, trap failure, and drain system constraint violations. | Separator DP, drain flow, trap status, acoustic/vibration, condensate level | Alarm precision >= 80% for labeled events; no unsafe auto-actions |
| FR-06 | Provide control recommendations (supervisory) to maintain quality: drain/valve sequencing, load ramp limits, desuperheater governance, reheat setpoints. | Actuator list; plant constraints; GL-003 optimizer | Recommendations respect constraints; operators can trace rationale |
| FR-07 | Emit standardized events and alarms to GL-003 and the plant HMI. | Event taxonomy; MQTT/Kafka/REST; alarm routing | Latency < 5 s for sensor-driven alarms; audit log complete |
| FR-08 | Maintain a quality KPI store and dashboards: min/avg dryness, excursions, energy and carbon impacts. | Time series store; metrics service; BI | Daily KPI rollups generated by 02:00 local time; accuracy validated |
| FR-09 | Model lifecycle management: versioning, deployment, rollback, and monitoring. | Model registry; CI/CD; feature store | Rollback within 15 min; drift alerting within 1 day |
| FR-10 | Site configuration management: per-header limits, sensor mappings, and actuator permissions. | Config service; CMDB; RBAC | Config changes auditable; can be promoted across environments |

# 7. Data Requirements

Steam quality control is data intensive. The module must operate in three modes depending on instrumentation maturity:

Mode A (Instrumented): direct moisture measurement or calorimeter exists at critical headers.

Mode B (Partially instrumented): standard P/T/flow plus separator/trap instrumentation; moisture inferred via soft sensors.

Mode C (Baseline): limited tags; only qualitative risk scoring and conservative alarms are possible.

## 7.1 Minimum viable tag set (per header)

Steam pressure (P_hdr) and temperature (T_hdr).

Steam mass flow or volumetric flow with density correction (F_hdr).

Upstream drum level (if boiler-supplied) and boiler load/firing rate (Load_boiler).

Separator differential pressure (DP_sep) and drain valve position (V_drain) where separators exist.

Condensate return conductivity (Cond_cond) and temperature (T_cond) where available.

## 7.2 Recommended tag set (improves accuracy and control)

Superheater outlet temperature and attemperator valve position (if present).

Steam trap state (open/closed), acoustic signature, or trap survey results.

Drip leg level/temperature, drain flow, and backpressure.

PRV inlet/outlet pressure and temperature (condensation risk across throttling).

Analyzer values: silica, sodium, dissolved solids, pH, dissolved oxygen in steam/condensate.

Ambient temperature, humidity, and wind (distribution heat loss, condensation risk).

Maintenance work orders and operator logs tagged to assets and timestamps.

## 7.3 Data dictionary (core)

| Tag (logical) | Description | Units | Typical rate | Required | Notes |
| --- | --- | --- | --- | --- | --- |
| P_hdr | Steam header pressure | bar(g) or kPa | 1-5 s | Yes | Prefer absolute in computations; ensure conversion |
| T_hdr | Steam header temperature | C | 1-5 s | Yes | Used for superheat margin and state detection |
| F_hdr | Steam flow | kg/s or t/h | 1-5 s | Yes* | If unavailable, infer from other balance points with lower confidence |
| P_prv_in / P_prv_out | PRV inlet/outlet pressure | bar(g) | 1-5 s | No | Used to assess condensation and flash |
| T_prv_in / T_prv_out | PRV inlet/outlet temperature | C | 1-5 s | No | Superheat margin change across valve |
| Level_drum | Boiler drum level | % or mm | 1-5 s | No | Strong driver of carryover risk |
| Load_boiler | Boiler firing/load | % or MW | 1-5 s | No | Correlates with transients and separation stress |
| DP_sep | Separator differential pressure | kPa | 1-5 s | No | Flooding or plugging indicator |
| V_drain | Drain valve position/command | % | 1-5 s | No | Actuator for moisture removal |
| Trap_status | Steam trap health/state | enum/bool | survey/daily | No | Often intermittent; integrate surveys |
| Moist_meas | Direct moisture or quality measurement | % moisture or x | 1-60 s | Optional | If present, becomes calibration reference |
| Cond_cond | Condensate conductivity | uS/cm | 1-60 min | Optional | Lagging indicator of carryover/contamination |
| SiO2 / Na | Silica / sodium in steam/condensate | ppb | 5-60 min | Optional | Critical for turbine protection where used |
| Ambient_T / RH | Ambient temperature / humidity | C / % | 1-15 min | Optional | Distribution loss and condensation risk |

## 7.4 Data quality, governance, and retention

Time synchronization: all OT sources must be aligned to a common clock (NTP/PTP).

Unit normalization: enforce a single canonical unit system internally (recommend SI: kPa(abs), C, kg/s).

Sensor health: compute missingness, stuck sensor detection, calibration drift, and range checks.

Data lineage: every metric produced must be traceable to input tags, model version, and configuration version.

Retention: raw 1-5 s data retained >= 13 months for seasonal analysis; derived KPIs retained >= 5 years.

Privacy/security: OT data treated as sensitive; follow IT/OT segmentation and RBAC.

# 8. Thermal, Thermodynamic, and Mathematical Foundations

## 8.1 Steam state determination

At each timestamp, determine the steam state using pressure P and temperature T. Use a validated steam property library (IAPWS-IF97 or equivalent).

Compute saturation temperature: T_sat = f_sat(P).

Compute superheat margin: DeltaT_sh = T - T_sat.

If DeltaT_sh > DeltaT_threshold (configurable, e.g., 3 C), treat steam as superheated for control logic (x = 1) but still compute carryover risk.

If DeltaT_sh approximately 0, treat steam as saturated and allow wet-steam dryness estimation.

## 8.2 Dryness fraction definition and key equations

For a saturated mixture at pressure P, the specific enthalpy h_mix is:

h_mix(P, x) = h_f(P) + x * h_fg(P)
=> x = (h_mix - h_f) / h_fg

Where h_f is saturated liquid enthalpy and h_fg is latent heat of vaporization at pressure P.

## 8.3 Measurement methods (reference instrumentation)

When available, use reference methods for calibration and audit:

Throttling calorimeter: an isenthalpic expansion from (P1, wet) to (P2, superheated). Compute h2 from (P2,T2), set h1 = h2, then compute x at P1.

Separating and throttling calorimeter: improves accuracy for very wet steam by removing entrained water before throttling measurement.

Optical or microwave moisture meters: direct measurement of droplet concentration/attenuation (instrument-specific calibration required).

Laboratory sampling (where feasible): condensate contamination indicators (silica/sodium) for carryover validation.

## 8.4 Soft sensor approach (physics-guided estimation)

Most plants do not have continuous calorimetry. Therefore, GL-012 scope emphasizes a hybrid soft sensor that combines physics and data-driven inference.

Physics layer: compute steam properties, superheat margin, and constraint checks from P/T/flow and equipment models.

State estimation layer: estimate latent moisture and carryover risk as hidden states using filtering (Kalman/EKF/UKF) or probabilistic regression.

Data-driven correction: learn residual error patterns from historical validated periods to reduce bias and improve robustness.

Uncertainty: report confidence intervals using model variance, sensor uncertainty, and data quality flags.

## 8.5 Separator and drain system modeling (control-oriented)

Model the separator/scrubber and drain system as a mass balance with constraints.

Let m_in be total mass flow into separator; moisture_in = (1 - x_in) * m_in
Moisture removed by separator/drains: m_removed = eta_sep * moisture_in (bounded by drain capacity)
Moisture out: moisture_out = moisture_in - m_removed
Dryness out: x_out = 1 - (moisture_out / m_out)

eta_sep is not constant; it depends on velocity, pressure, separator condition, and drain backpressure. The module must estimate eta_sep online.

## 8.6 Uncertainty propagation (required for trustworthy decisions)

When computing x or risk scores, propagate uncertainty from sensors and model parameters. At minimum:

Maintain per-sensor uncertainty (sigma_P, sigma_T, sigma_F) based on calibration specs and drift detection.

Compute sensitivity of key metrics to inputs (partial derivatives) and approximate variance via first-order propagation.

Surface uncertainty on dashboards and in advisories (e.g., x_est = 0.985 +/- 0.005).

# 9. AI/ML Requirements (inside GL-003)

AI/ML is used to estimate unmeasured quality variables, predict future excursions, and explain root causes. Models must be physics-guided, auditable, and fail-safe.

## 9.1 Priority ML use cases

Soft sensor for dryness fraction x (saturated/wet regions) with uncertainty.

Carryover event detection (classification) and early warning (time-to-event prediction).

Separator/trap health analytics (anomaly detection and failure probability).

Recommendation ranking: choose the lowest-cost action that restores quality within constraints.

## 9.2 Model families (recommended)

Hybrid regression: physics features + gradient boosting / random forest for residual correction.

Probabilistic models: Gaussian process regression or quantile regression for confidence intervals.

Temporal models: LSTM/TCN for short-horizon predictions, constrained by physics features.

Filtering/state estimation: EKF/UKF to combine noisy sensors with dynamics.

Unsupervised: isolation forest/autoencoder for anomaly detection on separator/trap signals.

## 9.3 Feature engineering (must-have)

Steam property features: T_sat(P), DeltaT_sh, enthalpy h(P,T), entropy s(P,T), density.

Transient indicators: rolling std/derivative of P and T, valve position rates, load ramp rate.

Equipment condition proxies: separator DP trend, drain valve duty cycle, trap survey age.

Cross-stream correlations: condensate conductivity response lag vs header conditions.

Ambient modifiers: temperature/humidity for distribution losses.

## 9.4 Data labeling and ground truth strategy

Quality labels are scarce. The program must create a labeling plan that combines:

Reference measurement campaigns (calorimeter/moisture meter) to generate high-quality labels for model calibration.

Event logs: operator-confirmed carryover, water hammer, turbine wetness alarms, separator flooding, trap failures.

Weak supervision: rules based on chemistry analyzers (silica/sodium spikes), condensate conductivity, and known operating patterns.

Synthetic data from first-principles simulation/digital twin for rare-event augmentation (with clear provenance).

## 9.5 Evaluation, monitoring, and MLOps

Offline: MAE/bias for x; precision/recall and time-to-detect for events; calibration of probability outputs.

Online: drift detection on features and residuals; weekly model health report; auto-alert and rollback.

Governance: model registry with versioning, training data snapshot, and approval workflow.

Explainability: feature importance and counterfactual explanations for recommendations (operator trust requirement).

Safety gating: ML outputs must be bounded and sanity-checked against physics constraints before reaching control logic.

# 10. Control Strategy and Actuation

## 10.1 Control layers

Steam quality control is implemented as a layered architecture:

Layer 0 (Protection/SIS): hard safety interlocks and trips. Not modified by this module.

Layer 1 (Regulatory control): PID loops in DCS/PLC (e.g., drum level, attemperator control, drain valve).

Layer 2 (Supervisory quality control - this module): compute constraints, recommend setpoint adjustments, and coordinate actions across assets.

Layer 3 (Optimization - GL-003): global objective optimization (energy, cost, carbon) subject to quality constraints produced by this module.

## 10.2 Primary manipulators (site dependent)

Drain valve setpoints and sequencing for separators/scrubbers and drip legs.

Steam trap maintenance recommendations and bypass governance (not continuous actuation, but operational control).

Desuperheater/attemperator setpoint bounds (avoid near-saturation at headers).

Header pressure/PRV setpoints and ramp rate limits during load changes (reduce condensation).

Reheater or steam dryer settings where installed.

Operational constraints: load ramp guidance, minimum superheat margin policies, insulation repair prioritization.

## 10.3 Control objectives and constraints

Maintain x >= x_min for each header/consumer class (configurable).

Maintain DeltaT_sh >= DeltaT_min for superheated operation where required (turbines).

Minimize energy losses from excessive draining, reheating, or over-superheating.

Respect drain capacity constraints (prevent flooding/backpressure).

Avoid actions that increase water hammer risk (rapid valve movements, cold starts without warm-up).

## 10.4 Recommended algorithms (pragmatic and deployable)

Rules + estimation: start with conservative rule-based gating using physics features; iterate with ML as confidence grows.

Constraint-based optimization (MPC-like): choose setpoint adjustments that satisfy quality constraints while minimizing penalty (energy, wear).

Event-driven control: during detected carryover risk, trigger a pre-approved mitigation playbook with clear operator confirmation requirements.

## 10.5 Fail-safe behavior

If data quality is degraded (missing P/T, sensor failure), the module must degrade gracefully: widen uncertainty, raise advisory, and avoid aggressive recommendations.

No direct closed-loop actuation without explicit site approval and safety review. Default is advisory mode.

All recommendations must include expected impact, confidence, and constraints checked.

Every automated action path (if enabled) must have an operator override and audit log.

# 11. Software and Integration Architecture (GL-003)

## 11.1 High-level data flow

OT Sensors/Analyzers -> Edge Collector -> Message Bus/Stream -> Feature Store ->
   SteamQualityEstimator (x, R_carry, eta_sep) -> QualityEvents/Alerts -> HMI/BI
                                          -> QualityConstraints -> GL-003 Optimizer -> Recommendations -> Ops Workflow

## 11.2 Module components (logical)

steam-quality-properties: steam table wrapper and thermodynamic computations (pure functions, unit-tested).

steam-quality-estimator: computes x_est, carryover risk, separator efficiency, uncertainty.

steam-quality-events: rules + ML event detection, severity scoring, and root cause hints.

steam-quality-control-advisor: converts events and constraints into recommended actions (playbooks).

steam-quality-config: per-site configuration, tag mapping, limits, and permissions.

steam-quality-metrics: KPI rollups, carbon/energy accounting, reporting endpoints.

## 11.3 Interfaces to GL-003 UNIFIEDSTEAM

The module must expose standardized outputs to the unified optimizer:

QualityConstraints: x_min(header), DeltaT_min(header), max drain duty cycle, max ramp rate, etc.

QualityState: x_est, R_carry, eta_sep, data_quality_flags, uncertainty bounds.

QualityEvents: event_type, severity, start/end timestamps, supporting evidence, recommended playbook.

QualityCosts: estimated energy penalty and CO2e impact for candidate mitigation actions (for optimizer objective).

## 11.4 Non-functional requirements

Latency: sensor-to-metric < 5 s for 1-5 s tags; event emission < 10 s.

Availability: 99.9% for core services; tolerate OT connectivity outages with buffering.

Determinism: property computations and constraint checks must be deterministic for auditability.

Security: run in IT/OT approved zones; encrypt in transit; RBAC for configuration and actions.

Observability: structured logs, metrics, traces; per-site health dashboards.

# 12. Team-by-Team Execution Plan

This section assigns work packages to each team. Deliverables are written as engineering artifacts with clear acceptance criteria.

## 12.1 RACI summary (workstreams)

The RACI matrix is provided in landscape for readability. Column abbreviations: Ops = Ops/Plant, Therm = Thermal Eng, Ctrl = Controls, Instr = Electrical/Instrumentation, Data = Data Engineering, ML = AI/ML, SW = Software, Clim = Climate Intelligence, Sec = Cybersecurity/IT-OT, QA = QA/Testing.

| Workstream | Ops | Therm | Ctrl | Instr | Data | ML | SW | Clim | Sec | QA |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Instr and tag mapping | A | C | R | R | C | I | I | I | C | C |
| Steam properties | I | A | C | C | I | C | R | I | I | C |
| Soft sensor (x, carryover) | C | C | C | I | R | A/R | C | I | I | C |
| Events and taxonomy | A | C | C | I | R | R | C | I | I | C |
| Control playbooks/constraints | A | C | A/R | C | C | C | R | C | I | C |
| Data pipeline/feature store | I | I | I | I | A/R | C | C | I | I | C |
| MLOps and governance | I | I | I | I | C | A/R | C | I | I | C |
| Dashboards and operator UX | A | C | C | I | C | C | A/R | I | I | C |
| Security/IT-OT deployment | I | I | I | I | I | I | C | I | A/R | C |
| Validation/commissioning | A | C | C | C | C | C | C | I | C | A/R |

RACI legend: R = Responsible, A = Accountable, C = Consulted, I = Informed.

## 12.2 Mechanical/Thermal Engineering

Own the physics: define quality limits, validate thermodynamic computations, and ensure recommendations reflect real equipment behavior.

### Key deliverables

Steam system P&IDs annotated with quality measurement/control points (per site).

Approved thermodynamic assumptions: saturation thresholds, target superheat margins, acceptable dryness per consumer class.

Separator and drain capacity model inputs (nameplate, sizing, constraints) and empirical adjustment factors.

Failure mode library: carryover causes, separator flooding mechanisms, water hammer precursors.

### Definition of done

Property calculations cross-checked against independent steam table references for a representative operating envelope.

Quality targets and constraints signed off by plant engineering and turbine/process owners.

Documented mapping from recommendations to physical mechanisms (why an action improves quality).

## 12.3 Controls/Automation Engineering (DCS/PLC)

Ensure the module can observe and influence the process safely. Maintain separation between advisory logic and safety/regulatory control.

### Key deliverables

Tag list and signal conditioning specifications (filtering, scaling, status bits).

Actuator inventory and permissions: which valves/setpoints can be recommended or automated, with interlocks and rate limits.

Implementation of any required additional measurements (DP, drain flow) and integration into DCS.

Operator playbooks and HMI integration requirements (alarm priorities, acknowledgement workflow).

### Definition of done

All proposed recommendation-to-actuator mappings reviewed for safety and operability.

Simulated scenarios demonstrate no adverse interactions with existing PID loops.

Clear rollback/disable path for advisory/automation features.

## 12.4 Electrical and Instrumentation

Provide reliable measurement of the variables that drive quality estimation and control.

### Key deliverables

Instrumentation gap assessment: where moisture/quality measurement is needed and what is feasible.

Calibration and maintenance plan for P/T/flow, analyzers, moisture meters, DP transmitters, and trap monitoring sensors.

Metadata capture: instrument type, range, accuracy, calibration dates, and failure modes.

Commissioning checklists for sensors and data acquisition.

### Definition of done

Critical sensors meet accuracy and response time requirements; calibration certificates recorded.

Signal quality flags implemented and validated (bad PV, out-of-range, maintenance mode).

Documented sensor uncertainty values delivered to AI/ML and analytics teams.

## 12.5 Data Engineering

Deliver the data foundation: ingestion, normalization, storage, feature serving, and governance.

### Key deliverables

Canonical tag dictionary and unit standard (SI internal units).

Edge-to-cloud (or edge-to-datacenter) streaming pipeline with buffering and replay.

Time alignment and resampling logic for mixed-rate signals.

Feature store tables for model training and online inference, with lineage.

Event store for alarms, operator actions, and maintenance records.

### Definition of done

End-to-end pipeline validated with backfill and real-time data; data loss < 0.1% during normal operation.

Schema versioning and backward compatibility implemented.

Data quality dashboards and automated checks running in production.

## 12.6 AI/ML Engineering

Build and maintain the hybrid models for x estimation, carryover risk, and equipment health analytics.

### Key deliverables

Model specification and training notebooks/pipelines (reproducible).

Ground truth plan: reference measurement campaign design and weak supervision rules.

Model artifacts registered with metadata (training set, features, hyperparameters, evaluation).

Online inference service with uncertainty outputs and drift monitoring.

Model explainability package for ops-facing reasoning.

### Definition of done

Model meets KPI acceptance thresholds on pilot sites.

Robustness tests passed: sensor dropout, drift, and abnormal operations.

MLOps runbook and rollback procedure validated in staging.

## 12.7 Software Development (Platform, Services, Edge)

Implement production-grade services, APIs, and user experiences; integrate tightly with GL-003.

### Key deliverables

Service implementations for module components (estimator, events, advisor, metrics).

API contracts (QualityState, QualityConstraints, QualityEvents) and client SDK usage inside GL-003.

Configuration service integration and RBAC enforcement for actions and limits.

Observability (logging/metrics/tracing) and SRE runbooks.

Edge deployment packages and upgrade mechanism for OT-adjacent collectors.

### Definition of done

All services pass CI/CD with unit/integration tests and security scans.

Latency and availability targets met under load test.

Backward compatible API versioning implemented for GL-003 integration.

## 12.8 Intelligence and Analytics

Convert raw detections into operational insight and root-cause analysis that can be trusted by operators and engineers.

### Key deliverables

Root-cause templates for quality excursions (e.g., high drum level, separator flooding, PRV condensation, trap failure).

Correlation and causal analysis routines for post-event review.

Automated incident reports with evidence bundles (plots, contributing factors, timeline).

### Definition of done

Post-mortem reports generated automatically for pilot incidents and accepted by plant SMEs.

Analytics outputs are explainable and traceable to data and assumptions.

## 12.9 Climate Intelligence

Quantify and optimize the climate and energy implications of steam quality actions.

### Key deliverables

Carbon accounting methodology for steam quality improvements (fuel savings, reduced blowdown losses, avoided rework).

Marginal emissions factors per site and time (where available) and integration into GL-003 objective.

Dashboards that translate quality control actions into energy and CO2e impact.

### Definition of done

Methodology reviewed by sustainability leadership and is auditable.

Reported savings reconcile with energy meters within agreed tolerance.

## 12.10 Cybersecurity and IT/OT

Ensure secure and compliant deployment in OT environments.

### Key deliverables

Network zoning and data diode/DMZ architecture for OT connectivity.

Certificate management, secrets handling, and RBAC integration.

Threat model and security controls for data and recommendation channels.

Incident response procedure and patch management plan.

### Definition of done

Security review passed for pilot site; penetration test findings resolved.

No direct control actions can bypass approved safety and access controls.

## 12.11 QA, Testing, and Commissioning

Validate correctness, safety, and operational value before scale rollout.

### Key deliverables

Test harness for steam property computations and unit conversions.

Synthetic scenario library (carryover, trap failure, PRV condensation, cold start) for regression testing.

Hardware-in-the-loop (HIL) or digital twin integration for supervisory control testing.

Commissioning scripts and acceptance test protocols for pilot sites.

### Definition of done

All acceptance tests passed; pilot sign-off obtained from plant operations.

Known limitations documented; monitoring and fallback behaviors verified.

# 13. Event Taxonomy, Severity, and Operator Workflow

A standardized taxonomy is required so GL-003, dashboards, and plant HMIs can interpret quality conditions consistently.

## 13.1 Core event types

| Event Type | Trigger (example) | Severity basis | Evidence to attach | Typical mitigation playbook |
| --- | --- | --- | --- | --- |
| LOW_DRYNESS | x_est < x_min for > N seconds | distance below limit + duration + consumer criticality | x_est, P/T, uncertainty, reference meas if any | Increase draining, reduce ramp rate, verify separator/traps |
| CARRYOVER_RISK_HIGH | R_carry > threshold | probability + confidence + downstream risk | risk score drivers (drum level, DP_sep, chemistry) | Stabilize drum level, check foaming, inspect separator drains |
| SEPARATOR_FLOODING | DP_sep high + drain capacity exceeded | risk of liquid transport | DP trend, drain valve duty, condensate level | Open drains per policy, reduce load, dispatch maintenance |
| TRAP_FAILURE_SUSPECTED | trap anomaly score high | steam loss vs water hammer risk | acoustic/vibration, temperature, survey history | Schedule trap repair, isolate/bypass per SOP |
| PRV_CONDENSATION_RISK | DeltaT_sh low and large pressure drop | condensation likelihood | P_in/out, T_in/out, valve position | Increase upstream superheat, adjust PRV staging, warm-up |
| WATER_HAMMER_RISK | pressure spikes + cold line indicators | safety risk | pressure transient waveform, line temperature | Slow valve movements, verify drip legs, warm-up procedure |
| ANALYZER_SPIKE | silica/sodium spike | turbine contamination risk | analyzer value + calibration status | Investigate carryover, chemistry control, consider turbine protection actions |
| DATA_QUALITY_DEGRADED | missing/stuck sensor | trust level | tag health summary | Switch to conservative mode; dispatch instrument tech |

## 13.2 Severity levels and notification policy

S0 - Informational: no action required; log only.

S1 - Advisory: operator awareness; recommendation provided.

S2 - Warning: action recommended within defined time; escalate to shift lead.

S3 - Critical: immediate action required; follow emergency/asset protection SOP; notify engineering leadership.

Severity thresholds are configured per site and consumer criticality. The module must avoid alarm flooding by using hysteresis, rate limits, and event correlation.

# 14. Validation, Testing, and Acceptance Plan

## 14.1 Test phases

Phase 0 - Offline validation: historical replay with labeled events and reference measurement periods.

Phase 1 - Shadow mode: run online, produce metrics and advisories without impacting operations; collect operator feedback.

Phase 2 - Advisory mode: operators execute recommendations manually; measure outcome and refine playbooks.

Phase 3 - Limited automation (optional): enable pre-approved setpoint adjustments with tight bounds and immediate rollback.

Phase 4 - Scale rollout: replicate across units with configuration templates and site-specific tuning.

## 14.2 Acceptance tests (minimum)

Steam property correctness: compare property outputs to independent reference across operating envelope.

Dryness fraction validation: compare x_est to calorimeter/moisture meter data; verify uncertainty calibration.

Event detection: demonstrate time-to-detect and recall/precision on known incidents.

Control recommendation safety: demonstrate constraint checks prevent unsafe suggestions; verify rate limits.

Resilience: simulate sensor dropout and network outages; verify graceful degradation and buffering.

Security: validate RBAC, audit logging, and encryption; confirm no unauthorized control path exists.

Performance: load test at expected tag counts and sampling rates; verify latency/availability.

## 14.3 Reference measurement campaign (pilot requirement)

At least one pilot site must execute a reference measurement campaign to establish ground truth. Recommended plan:

Select 1-3 critical headers (including at least one turbine header if applicable).

Run calorimeter or moisture meter measurements across multiple load conditions (steady and transient).

Record concurrent P/T/flow, drum level, separator DP, and chemistry analyzers.

Store data with precise timestamps and instrument metadata; label operating regimes and anomalies.

Use results to calibrate and validate soft sensors; document bias and confidence intervals.

# 15. Deployment and Operations

## 15.1 Deployment topology

Edge collector runs inside OT/DMZ to ingest high-rate tags and buffer during outages.

Core inference services can run on-prem or in a secure cloud depending on site policy; latency targets must still be met.

Configuration, model registry, and dashboards may be centralized with site-specific access controls.

## 15.2 Operational runbooks

Daily: review quality KPIs and top events; confirm no persistent DATA_QUALITY_DEGRADED flags.

Weekly: review model health/drift report; validate against any spot measurements or operator observations.

Monthly: correlate events with maintenance; update trap/separator health baselines; review carbon accounting.

Incident: if critical quality event occurs, generate evidence bundle and initiate post-mortem within 72 hours.

## 15.3 Change management

Configuration changes require approval and are deployed via versioned config packages.

Model updates follow MLOps approval gates and canary deployment per site.

Playbook changes must be reviewed by operations and controls engineering.

All changes must be auditable and reversible.

# 16. Risk Register and Mitigations

| Risk | Impact | Likelihood | Mitigation | Owner |
| --- | --- | --- | --- | --- |
| Insufficient instrumentation for moisture/quality | Low accuracy and limited control value | Medium | Adopt staged modes A/B/C; prioritize instrumentation gaps at pilot sites | Instr/Plant Eng |
| Sensor drift and bad data | False alarms or missed events | High | Sensor health monitoring, calibration program, uncertainty propagation, conservative fallback | Data Eng + Instr |
| Model overfitting / poor generalization across sites | Operational distrust; poor performance | Medium | Physics-guided features, cross-site validation, site-specific calibration | AI/ML |
| Unsafe or impractical recommendations | Safety risk; adoption failure | Low-Med | Hard constraint checks, operator confirmation, controls review, playbook governance | Controls + Ops |
| OT cybersecurity constraints block deployment | Schedule delay | Medium | Early security architecture design; DMZ patterns; minimal OT footprint | Sec/IT-OT |
| Lack of ground truth for validation | Cannot prove value | Medium | Reference measurement campaigns; weak supervision; incident labeling | Program + AI/ML |
| Alarm fatigue | Operators ignore alerts | Medium | Severity design, hysteresis, correlation, user testing | Ops + Software |
| Integration mismatch with GL-003 APIs | Rework and delays | Medium | Contract-first design; shared schema repo; automated integration tests | Software |
| Carbon accounting disputes | Loss of credibility | Low-Med | Auditable methodology; reconcile with meters; transparent assumptions | Climate Intelligence |
| Pilot site operational constraints | Limited testing windows | High | Shadow mode first; coordinate with outages/turnarounds; staged rollout | Program + Ops |

# 17. Roadmap to Q2 2026 (Execution Milestones)

Dates are indicative and should be aligned with the portfolio master schedule. Focus is on achieving a validated pilot and production-ready module by end of Q2 2026.

| Timeframe | Milestone | Key outputs | Go/No-Go criteria |
| --- | --- | --- | --- |
| Dec 2025 - Jan 2026 | Requirements and site selection | Pilot site selected; tag list; instrumentation gap plan; API contracts drafted | Ops/Engineering sign-off; security architecture approved |
| Feb 2026 | Data foundation MVP | Edge ingestion live; canonical units; property library; KPI skeleton | Data availability >= 95% for critical tags in pilot |
| Mar 2026 | Estimation MVP (shadow mode) | Baseline x_est and R_carry outputs; event taxonomy; dashboards in read-only | Model outputs stable; no critical data quality blockers |
| Apr 2026 | Validation campaign | Reference measurement campaign executed; model calibration and error report | Bias and uncertainty meet thresholds; evidence pack complete |
| May 2026 | Advisory mode pilot | Operator playbooks; recommendations with rationale; measured improvements | Operator acceptance; reduction in excursions or improved response time |
| Jun 2026 | GL-003 integrated release candidate | Quality constraints integrated into optimizer; production hardening; runbooks | All acceptance tests passed; rollback verified |
| End of Q2 2026 | Release and scale plan | Release notes; replication template; backlog for next sites | Steering committee sign-off; funding and site pipeline confirmed |

# Appendix A. Example Computations (Procedural)

This appendix provides procedural examples without hard-coded steam table numbers. Use the approved property library for numeric values.

## A1. Superheat margin

Inputs: P_hdr, T_hdr

Steps:

Compute T_sat = saturation_temperature(P_hdr).

Compute DeltaT_sh = T_hdr - T_sat.

If DeltaT_sh > threshold, classify as superheated; else saturated/wet.

## A2. Throttling calorimeter dryness fraction

Inputs: upstream pressure P1, downstream pressure P2, downstream temperature T2.

Steps:

Compute h2 = enthalpy(P2, T2) (should be superheated after throttling).

Set h1 = h2 (isenthalpic throttling assumption).

Compute h_f and h_fg at P1 (saturated properties).

Compute x = (h1 - h_f) / h_fg; clamp to [0,1].

Report x with uncertainty based on sensor errors and validity checks (e.g., confirm downstream is superheated).

# Appendix B. Glossary (selected)

| Term | Definition |
| --- | --- |
| Dryness fraction (x) | Mass fraction of vapor in a saturated mixture; x = 1 means no liquid water present at equilibrium. |
| Carryover | Transport of liquid droplets and dissolved/entrained solids with the steam flow. |
| Water hammer | Pressure surge caused by rapid condensation or acceleration of liquid slugs in piping. |
| Superheat | Steam temperature above saturation temperature at the same pressure. |
| Separator | Mechanical device to remove entrained moisture from steam. |
| Steam trap | Automatic valve that discharges condensate while retaining steam. |
| Soft sensor | Model-based estimator of a variable that is not directly measured. |
| Uncertainty bound | Quantified confidence interval around an estimate, based on sensor/model uncertainty. |