GL-005 — COMBUSENSE
CombustionDiagnosticsAgent

Design & Delivery Playbook (All Teams)
Combustion Diagnostics • CQI Scoring • Anomaly Detection • Explainability • SIL 2 Safety Boundary • Streaming via SSE

Document date: December 18, 2025  |  Target delivery: Q2 2026  |  Status: Implemented (per agent registry)

# 1. Agent Overview

| Field | Value |
| --- | --- |
| Agent ID | GL-005 |
| Codename | COMBUSENSE |
| Agent Class | CombustionDiagnosticsAgent |
| Domain | Combustion |
| Type | Analyzer |
| Complexity | Medium |
| Priority | P1 |
| Business Value (indicative) | $8B |
| Target Release | Q2 2026 |
| Maturity Score | 92 |
| Lifecycle Status | Implemented |

High-level description:

Standalone combustion diagnostics with Combustion Quality Index (CQI) scoring; SHAP/LIME explainability; real-time anomaly detection; attention visualization; IEC 61511 SIL 2 safety boundary compliance; natural-language explanations; and streaming diagnostics via Server-Sent Events (SSE).

Primary inputs (minimum viable signal set):

Fuel flow

Combustion air flow

O₂ (flue gas)

CO (flue gas)

NOₓ (flue gas)

Flame signals (e.g., UV/IR, scanner intensity, flicker)

Safety interlocks (SIS statuses, bypass states)

Burner status (on/off, mode, permissives)

Combustion air temperature

Primary outputs:

CQI score (0–100) with sub-scores

Anomaly alerts with severity and confidence

Diagnostic reports (root cause hypotheses, recommended checks)

Safety compliance status (boundary monitoring, interlock health signals)

Explainability visualizations (SHAP/LIME feature attributions)

Natural-language summaries (operator-ready)

Attention maps (signal/time-step importance)

Streaming updates (SSE) + optional Kafka topics

Integration targets:

DCS

PLC

Combustion analyzers (CEMS / flue gas analyzers)

SIS (Safety Instrumented System)

OPC-UA

Kafka

SSE streaming consumers (dashboards, HMI overlays, chat/assistant front-ends)

# 2. Purpose, Audience, and Working Assumptions

Purpose:

This document is the shared implementation guide for GL-005 (COMBUSENSE). It defines what each team must deliver, the required data and engineering foundations, the mathematical/ML approach, safety boundaries, real-time architecture, and validation/acceptance criteria. The intent is to align AI, software, OT/controls engineering, safety engineering, data engineering, climate intelligence, and program teams to a single executable plan.

Primary audiences (teams):

AI/ML (modeling, explainability, MLOps)

Software Engineering (services, APIs, UI, streaming, integration)

Data Engineering (ingestion, quality, storage, governance)

Controls/OT Engineering (DCS/PLC, tag mapping, operating modes, instrumentation)

Combustion & Thermal Engineering (domain physics, KPIs, diagnostics logic)

Safety Engineering (IEC 61511, SIL 2 boundary, hazard/risk assessments)

Cybersecurity / OT Security (network zoning, identity, monitoring)

Climate Intelligence (emissions accounting, reporting, optimization insights)

QA/Validation (test design, acceptance, regression)

Product/Program/Operations (requirements, rollout, training, support)

Working assumptions and constraints:

GL-005 is a diagnostic/advisory system. It must not directly actuate burners, valves, dampers, or safety interlocks.

SIS logic and final protective actions remain exclusively within the SIS; GL-005 may read SIS states but shall not modify them.

Deployment must support near-real-time processing (typical target ≤ 2 s end-to-end latency for alerts; configurable per site).

All calculations must be unit-consistent and site-calibrated; tag mapping is plant-specific and must be controlled via configuration, not code changes.

Explainability outputs are required for operator trust and for engineering auditability (SHAP/LIME + attention-based views).

Safety compliance status is monitoring-oriented (bypass detection, interlock health indicators, operating envelope checks), not SIL function execution.

# 3. Problem Statement and Target Outcomes

Industrial combustion systems frequently operate with:

Excess air outside optimal band → efficiency loss, higher fuel cost, increased CO₂.

Incomplete combustion → elevated CO, flame instability, potential safety risks.

High NOₓ episodes → compliance risk and environmental cost.

Sensor drift or analyzer faults → misleading operator decisions.

Mode transitions (startup/shutdown/load swings) → transient instabilities and nuisance trips.

Limited root-cause visibility → repeated events and longer mean time to repair (MTTR).

GL-005 target outcomes (what “good” looks like):

A real-time Combustion Quality Index (CQI) that is stable, interpretable, and tied to actionable drivers (air–fuel balance, emissions, stability).

Early detection of abnormal combustion and instrument faults with controlled false-alarm rates.

Operator-ready explanations: what changed, why it matters, and what to check next.

Safety boundary monitoring aligned with IEC 61511 / SIL 2 governance (e.g., interlock bypass visibility, envelope excursions) without interfering with SIS.

Streaming diagnostics consumable by dashboards/HMIs and downstream analytics (SSE; optional Kafka).

Climate intelligence outputs: CO₂/NOₓ/CO intensity tracking and evidence for emissions reductions.

Key performance indicators (KPIs):

CQI availability (% time CQI produced within latency SLA).

Alert precision/recall (per anomaly type) and nuisance alarm rate (alarms/day/unit).

Detection lead time vs. existing alarms/trips (minutes).

Reduction in CO excursions and NOₓ exceedances (ppm-hours or % time in violation band).

Fuel efficiency improvement proxy (excess-air control stability, CO reduction, reduced O₂ drift) — quantified per site.

MTTR for recurrent combustion issues (hours) and recurrence frequency.

# 4. Scope, Boundaries, and Non-Goals

In scope:

Compute CQI score and sub-scores from live and historical signals.

Detect anomalies across combustion performance, emissions behavior, flame stability, and sensor/actuator inconsistencies.

Provide diagnostic hypotheses and recommended checks (rule-based + ML-informed).

Generate explainability artifacts (SHAP/LIME, attention maps) for each significant event and for CQI degradation.

Expose outputs via SSE and optional Kafka topics; produce periodic reports (shift/day/week).

Monitor safety boundary indicators: interlock status patterns, bypass detection, envelope excursions, and data integrity for safety-related signals.

Explicit non-goals (must remain out of scope unless separately authorized and safety-certified):

Closed-loop combustion control (air/fuel setpoint manipulation).

Direct actuation of fuel valves, dampers, or burner management sequences.

Replacing OEM Burner Management System (BMS) logic, SIS logic, or proof-test procedures.

Serving as a Safety Instrumented Function (SIF) element or SIL-rated device.

Operator instructions that override established operating procedures without engineering approval.

# 5. System Context and Reference Architecture

GL-005 sits between plant operational technology (OT) data sources and downstream consumers (operators, engineers, climate reporting, maintenance). It ingests time-series signals, computes physics-informed features, scores combustion quality (CQI), detects anomalies, generates explanations, and streams results.

Reference architecture (typical deployment):

Key architectural principles:

Read-only integration to OT control layers (DCS/PLC/SIS) unless explicitly approved and engineered.

Edge-first processing for low latency and OT network containment; cloud optional for fleet analytics.

Deterministic signal conditioning and physics features ahead of ML to reduce model brittleness.

Model outputs are accompanied by explanations and confidence estimates.

Event-driven design: anomalies produce structured events usable by HMIs, dashboards, and ticketing systems.

# 6. Data Requirements (Signals, Semantics, Quality, and Governance)

GL-005 performance is dominated by signal quality. The minimum viable signal set (MVSS) must be available with stable calibration and clear units/metadata. All teams should treat data readiness as a gating milestone.

## 6.1 Minimum Viable Signal Set (MVSS)

| Signal | Required semantics / units | Typical sampling | Source | Minimum quality checks |
| --- | --- | --- | --- | --- |
| Fuel flow | Mass flow (kg/s) or standard volumetric (Nm³/h); include fuel type and LHV/HHV metadata | 1–5 s | DCS/PLC flowmeter | Range, rate-of-change, zero/negative, sensor stuck |
| Combustion air flow | kg/s or Nm³/h; ideally mass-compensated | 1–5 s | DCS/PLC | Range, damper/FD fan consistency, sensor stuck |
| Combustion air temperature | °C | 1–5 s | DCS/PLC | Range, sensor drift |
| O₂ (flue gas) | vol% dry basis; analyzer status required | 5–15 s | Combustion analyzer/CEMS | Calibration status, plausibility (0–21%), step changes |
| CO (flue gas) | ppm dry basis (or mg/Nm³); analyzer status required | 5–15 s | Combustion analyzer/CEMS | Zero/span drift, negative values, spikes during purge |
| NOₓ (flue gas) | ppm as NO₂ equivalent; dry basis; analyzer status required | 5–15 s | Combustion analyzer/CEMS | Calibration status, saturation, invalid flags |
| Flame signal(s) | Flame on/off + analog intensity/flicker metric | 0.1–1 s (if available) else 1–5 s | BMS / flame scanner | Dropouts, flicker anomalies, compare redundant scanners |
| Burner status | State machine: purge/ignite/run/trip; firing rate; # burners in service | 1–5 s | BMS/DCS | State validity, illegal transitions |
| Safety interlocks | Binary/permissive statuses; bypass status; trip history events | Event-driven + 1–5 s snapshot | SIS/BMS | Bypass detection, inconsistent status, timestamp accuracy |

## 6.2 Strongly Recommended Additional Signals (for higher diagnostic accuracy)

Flue/stack gas temperature (°C) and/or boiler/furnace outlet temperature

Furnace/stack draft (pressure), damper positions, FD/ID fan speeds

Fuel gas pressure/temperature, viscosity/density corrections (for liquids)

Boiler load proxy (steam flow, firing demand, MW), excess-air trim setpoints

Atomizing steam/air flow (for liquid fuels), burner register positions

Analyzer health tags: calibration mode, sample pump status, fault codes

Ambient temperature/pressure/humidity (for air density correction)

Start/stop commands, trip codes, alarm/event logs from DCS/BMS/SIS

## 6.3 Data Contract (canonical record)

To prevent repeated integration work, all ingested data should be normalized into a canonical time-series record. At minimum:

asset_id (unit/burner identifier)

timestamp_utc (or timestamp with explicit timezone) + source timestamp

tag_id / tag_name + source_system (DCS/PLC/SIS/CEMS)

value (float/int/bool) + unit + engineering_range

quality_code (Good/Bad/Uncertain) + detailed reason if Bad

sample_period and ingestion_latency

calibration/status flags for analyzers (O₂/CO/NOₓ) and flame scanner

## 6.4 Data Quality Gate (must-pass before model sign-off)

≥ 95% Good-quality samples for MVSS tags during steady operation windows.

Time alignment: inter-signal timestamp skew ≤ 1 sample period (or corrected via alignment).

No persistent unit ambiguity (e.g., CO in ppm vs mg/Nm³).

Analyzer calibration and invalid states are explicitly captured and excluded from scoring/alerts.

Operating mode labels available (startup/shutdown/purge/ignite/run) so models are not trained on mixed regimes unintentionally.

# 7. Combustion and Thermal Engineering Foundations (what the models must respect)

GL-005 must be grounded in combustion physics. Purely data-driven models will be brittle across fuels, loads, and seasons unless we embed the correct invariants and operating mode logic.

## 7.1 Core combustion quantities

Air–fuel ratio (AFR): AFR = (air mass flow) / (fuel mass flow). Must be computed in consistent mass units; volumetric flows require density/standardization.

Stoichiometric AFR (AFRₛₜ): Depends on fuel composition. For a generic fuel CₓHᵧO_zS_w: required O₂ moles = x + y/4 − z/2 + w. Stoichiometric air moles = O₂/0.21.

Excess air ratio (λ): λ = AFR / AFRₛₜ. λ > 1 is excess air; λ < 1 is fuel-rich.

Equivalence ratio (φ): φ = 1/λ. Many flame stability phenomena map more directly to φ.

O₂ trim / excess O₂: Flue-gas O₂ (dry) is an operational proxy for λ but must be interpreted with analyzer health and dilution/leakage considerations.

## 7.2 Emissions normalization (needed for fair scoring)

Regulatory and engineering comparisons often normalize emissions to a reference O₂ level (e.g., 3% O₂ for gas turbines or 15% O₂ for some boilers; site-specific). If O₂ is available, GL-005 should compute both raw and O₂-corrected values where appropriate.

Generic dry O₂ correction (example to reference O₂_ref):

C_corrected = C_measured × (21 − O₂_ref) / (21 − O₂_measured)

Where O₂ values are in percent (vol%). This formula is commonly used as an approximation; confirm site regulatory basis and whether wet/dry corrections apply.

## 7.3 Flame stability signals

Flame scanners provide a direct indicator of flame presence and quality but can be noisy; use filtered intensity + flicker metrics.

Key events: ignition failure, flameout, instability during load swings, burner-to-burner imbalance, pulsations.

Model features should include both absolute level and short-term variance / spectral energy bands (where sampling allows).

## 7.4 Thermal/instrumentation considerations (engineering requirements)

Combustion air temperature is required to correct air density and to interpret performance across seasons.

Analyzer response time and sample conditioning introduce lag; align O₂/CO/NOₓ with process signals using estimated delays (cross-correlation and known sample line time constants).

Define operating envelopes (min/max flows, permitted O₂ bands, analyzer valid ranges) per unit and per mode.

Include explicit handling of purge/ignition phases—emissions spikes in these phases should not be treated as normal combustion or as persistent faults unless durations exceed engineered limits.

Sensor calibration/proof-test events must be captured to avoid misclassifying calibration steps as anomalies.

# 8. CQI (Combustion Quality Index) — Definition, Mathematics, and Engineering Tuning

CQI is the primary operator-facing metric. It must be interpretable, stable, and tied to controllable drivers. CQI is not a single model output; it is a composite score combining physics-based computations, statistical health metrics, and (optionally) ML residual scoring.

## 8.1 CQI structure (recommended)

Recommended CQI decomposition:

CQI_total = w₁·CQI_efficiency + w₂·CQI_emissions + w₃·CQI_stability + w₄·CQI_safety + w₅·CQI_data

Where Σwᵢ = 1. Weights are site-tunable but must be governed (change control).

Suggested default weights (starting point; tune per unit):

| Component | Default weight |
| --- | --- |
| Efficiency / air–fuel optimality | 0.30 |
| Emissions (CO/NOₓ) | 0.30 |
| Stability (flame + variability) | 0.20 |
| Safety boundary status | 0.15 |
| Data integrity / confidence | 0.05 |

## 8.2 Example sub-score mappings (mathematical form)

Sub-scores should map engineering-relevant metrics into a 0–100 range using smooth, monotonic functions. This reduces “jumpiness” and supports explainability. Typical options: piecewise-linear penalty, logistic penalty, or clipped z-scores.

Example (piecewise) for O₂ band around a target O₂*:

Let O₂_low and O₂_high define the preferred band. Define penalty p_O2 = 0 when within band, increasing linearly outside band. Then CQI_efficiency = 100 × (1 − clip(p_O2, 0, 1)).

Example (logistic) for CO excursions (ppm):

CQI_CO = 100 / (1 + exp(k·(CO − CO_target))) where k tunes steepness. Similar for NOₓ.

Example stability score from flame signal variability:

Compute a rolling window standard deviation σ_flame over N seconds and normalize to a baseline σ₀. Define CQI_stability = 100 × exp(−α·max(0, (σ_flame/σ₀ − 1))).

## 8.3 Guardrails and caps

If any critical safety boundary condition is active (e.g., interlock bypass or trip state), cap CQI_total ≤ CQI_cap_safety (e.g., 30) and raise a Safety Compliance alert.

If analyzer status is invalid (calibration, fault), exclude that analyzer from scoring and reduce CQI_data proportionally; do not generate emissions-based alarms without valid sensors.

Compute CQI only in defined operating modes (e.g., RUN). Provide separate “startup CQI” or mode-specific scoring if required.

## 8.4 Engineering tuning workflow

Combustion/Thermal engineers define preferred bands/targets (O₂*, CO_target, NOₓ_target) by load and fuel type.

AI/ML team implements mapping functions and validates stability and sensitivity using historical data.

Controls engineering validates that CQI aligns with operator reality and existing KPIs; adjust weights and bands under change control.

Safety engineering reviews any safety-related caps/logic to ensure GL-005 remains advisory and does not conflict with IEC 61511 processes.

Finalize parameter sets per asset (unit/burner) and store in a versioned configuration repository.

# 9. Real-Time Anomaly Detection and Diagnostics

GL-005 must detect and explain abnormal conditions in real time. The recommended approach is layered: deterministic rule checks + statistical change detection + ML-based multivariate anomaly scoring. Layering reduces false positives and improves auditability.

## 9.1 Anomaly taxonomy (standardized event types)

| Event type | Description (operator meaning) |
| --- | --- |
| COMBUSTION_RICH | Low O₂ with elevated CO, possible fuel-rich operation, risk of CO excursions and instability. |
| COMBUSTION_LEAN | High O₂/excess air, efficiency loss, possible flame instability at low load. |
| CO_SPIKE | Transient CO spike beyond engineered threshold; may indicate poor mixing, ignition issues, or analyzer artifact. |
| NOX_EXCURSION | NOₓ beyond target band; may indicate high flame temperature, burner imbalance, or control issues. |
| FLAME_INSTABILITY | High flame flicker/variance or intermittent flame signal drops. |
| ANALYZER_DRIFT_O2/CO/NOX | Slow drift or step changes inconsistent with process; calibration/maintenance candidate. |
| FLOW_MISMATCH | Fuel/air relationship inconsistent with expected AFR curve by load (possible sensor fault or actuator issue). |
| MODE_SEQUENCE_ANOMALY | Illegal/rare state transitions in BMS/burner status. |
| SAFETY_BYPASS_ACTIVE | Safety interlock bypass detected or prolonged bypass. |
| DATA_QUALITY_DEGRADED | Missing data, bad quality codes, out-of-range, or timestamp skew. |

## 9.2 Detection layers

| Layer | Purpose |
| --- | --- |
| Layer 0 — Data integrity | Missing values, bad quality, timestamp skew, unit mismatch, stuck sensor, out-of-range. |
| Layer 1 — Deterministic envelope & state rules | Engineering bounds, interlock logic patterns, mode-specific constraints (purse/ignite/run). |
| Layer 2 — Statistical change detection | EWMA/CUSUM, rolling z-scores, change-point detection for drifts and shifts. |
| Layer 3 — Multivariate ML anomaly score | Autoencoders / isolation forest / one-class models / transformer residuals per operating mode. |
| Layer 4 — Diagnostic reasoning | Map anomaly signatures to hypotheses and recommended checks using rules + ML attributions (SHAP/LIME). |

## 9.3 Severity, confidence, and alert hygiene

Each anomaly event must include: severity (S1–S4), confidence (0–1), affected asset, start/end timestamps, and top contributing signals.

Use hysteresis and minimum duration rules to prevent chatter (e.g., condition must persist ≥ N seconds).

Deduplicate alerts: collapse repeated detections into a single incident with updates.

Implement a “quiet mode” during known transient phases (e.g., purge/ignite) while still monitoring safety boundaries.

Track false positives and operator feedback to continuously tune thresholds.

## 9.4 Diagnostics output structure

Each diagnostic report (per incident) should contain:

Incident summary (what happened, when, duration, severity).

CQI impact (drop amount, component contributions).

Top drivers (SHAP/LIME/attention) + engineering interpretation.

Root cause hypotheses ranked (with rationale and confidence).

Recommended checks/actions (site-approved; include safety warnings).

Evidence panel: key trends (O₂, CO, NOₓ, flows, flame signal) with annotations.

Data quality notes (invalid analyzer, missing signals, known maintenance activities).

# 10. Explainability, Attention Visualization, and Natural-Language Narratives

Explainability is mandatory. GL-005 must produce evidence that connects model outputs to underlying signals and engineering meaning. This includes feature attributions (SHAP/LIME), time-step importance (attention/gradients), and operator-ready narratives.

## 10.1 Explainability requirements

Provide local explanations for: (a) CQI degradation events, (b) each anomaly incident, and (c) any safety compliance status change.

Explanations must reference real signals and time windows (e.g., “CO increased from X to Y ppm over Z min”).

Explainability must be consistent with operating mode (avoid attributing purge behavior to normal run).

Store explanations with the incident for auditability; include model version and configuration version.

## 10.2 SHAP and LIME (how to use)

Recommended usage patterns:

Use SHAP for tree-based models (e.g., gradient-boosted trees) that predict CQI components or anomaly scores. SHAP provides stable feature attributions and supports global + local views.

Use LIME as a fallback for models where SHAP is computationally expensive or not supported, especially for per-incident explanations.

For time-series deep models, do not rely on classic SHAP/LIME directly; instead use time-series attributions (integrated gradients, occlusion) plus attention visualizations.

## 10.3 Attention maps and time-series attribution

If transformer/attention-based models are used, generate attention heatmaps across signals and time. Important caveat: attention weights are not always causal explanations; treat them as an interpretability aid and validate against perturbation tests.

Attention map axes: time window (e.g., last 2–10 minutes) × signals (flows, O₂, CO, NOₓ, flame, statuses).

Provide a top-N signal list and top contributing time segment(s).

Run periodic sanity checks: permute or occlude a signal and confirm anomaly score changes as expected.

## 10.4 Natural-language explanations (operator-ready)

Natural-language summaries should be generated from structured diagnostic facts (not free-form speculation). Two recommended approaches:

Template-first: deterministic templating with controlled vocabulary for safety-critical contexts.

LLM-assisted: an LLM produces narratives only from a constrained JSON “evidence bundle” and must follow safety rules (no direct actuation instructions, highlight uncertainty).

Minimum content of the evidence bundle for narratives:

Operating mode + load context

Key signal deltas (before/after, trend slope) for O₂/CO/NOₓ, flows, flame

Detected event type + severity + confidence

Top attributions (feature contributions) and associated time segments

Safety status summary (any bypass/trip active?)

Recommended checks list (pre-approved)

# 11. IEC 61511 / SIL 2 Safety Boundary Compliance

GL-005 must respect IEC 61511 functional safety principles. The agent is NOT a Safety Instrumented Function (SIF) and must not be credited for risk reduction unless formally engineered, assessed, and certified. In this program, GL-005’s safety role is boundary monitoring and situational awareness.

## 11.1 Safety boundary definition

GL-005 is advisory only. It may read SIS/BMS statuses but shall not write to SIS, BMS, PLC, or DCS control outputs.

GL-005 outputs must not be used as the sole basis to disable interlocks, bypass protections, or override procedures.

Any integration that could influence control actions (even indirectly) requires a separate hazard review and management of change (MOC).

## 11.2 Safety compliance monitoring (what GL-005 can report)

Interlock bypass active / prolonged bypass (with duration and tag evidence).

Repeated demands/trips on specific interlocks (early indicator of degrading equipment).

Illegal or rare BMS state transitions (e.g., repeated recycle events).

Loss of critical diagnostics (e.g., flame scanner unhealthy) during firing.

Out-of-envelope operation: flows or emissions outside engineered safe ranges (site-defined).

Data integrity issues for safety-related signals (bad quality, missing updates).

## 11.3 Required safety engineering deliverables

Safety Boundary Requirements Specification (SBRS): define what GL-005 monitors, thresholds, and response messaging.

Hazard & risk review (e.g., HAZOP/LOPA input): confirm GL-005 does not introduce new hazards and does not change risk credit.

Cybersecurity review for OT network connectivity, including read-only enforcement and credentialing.

Verification plan: test cases showing that GL-005 fails safe (diagnostics degrade gracefully) and does not affect SIS/BMS operations.

Audit trail design: every alert/report includes timestamp, tag evidence, configuration version, and model version.

## 11.4 Messaging and human factors (safety-critical UX rules)

Use clear severity labels and avoid ambiguous recommendations. Prefer “Check/Inspect/Verify” over “Do X immediately” unless the action is an established SOP.

Always show whether safety interlocks are active/bypassed and include a reminder that SIS/BMS remains authoritative.

Avoid alarm flooding: aggregate related alerts into incidents; provide suppression rules during known transitions.

# 12. Engineering Architecture, Integration, and Streaming Interfaces

## 12.1 Runtime components (logical services)

| Component | Responsibilities |
| --- | --- |
| Protocol/Tag Connector | OPC-UA client (and/or vendor protocols) that reads configured tags with quality codes; supports buffering and reconnect. |
| Signal Conditioning | Unit conversion, outlier handling, delay alignment, resampling, feature computation. |
| CQI & Anomaly Engine | Computes CQI, anomaly scores, incident lifecycle, and safety compliance status. |
| Explainability Service | Generates SHAP/LIME/attributions and attention visualizations for events; caches results. |
| Diagnostics API | Serves latest CQI and active incidents; exports reports; SSE endpoint for streaming. |
| Persistence | Time-series store (or historian) for CQI/anomaly outputs, incident DB, model/config registry. |
| UI / Dashboard (optional) | Operator and engineer views: live CQI, trend overlays, incident workbench, explainability panels. |

## 12.2 Integration patterns

OPC-UA read-only ingestion for DCS/PLC tags and statuses; map tags via configuration file per site.

Kafka as an optional backbone for scalable streaming, replay, and integration with other analytics.

SSE for low-latency delivery to web dashboards and lightweight clients; supports reconnection and last-event-id.

Optional REST endpoints for pull-based consumers (DCS summary pages, BI tools).

## 12.3 SSE event contract (example)

SSE provides a stream of JSON events. Each event must be small, self-contained, and versioned. Example event types: cqi_update, anomaly_start, anomaly_update, anomaly_end, safety_status, heartbeat.

event: cqi_update
id: 1734567890-assetA
data: {
  "schema_version": "1.0",
  "asset_id": "Boiler-3/Burner-2",
  "ts_utc": "2026-04-10T12:34:56Z",
  "cqi_total": 82.4,
  "cqi_components": {
    "efficiency": 85.1,
    "emissions": 78.2,
    "stability": 88.0,
    "safety": 95.0,
    "data": 90.0
  },
  "confidence": 0.86,
  "active_incidents": ["INC-2026-04-10-0012"]
}

## 12.4 Kafka topics (optional)

If Kafka is used, recommended topics:

gl005.raw.telemetry (normalized tag stream)

gl005.features (derived features per asset and time window)

gl005.cqi (CQI updates)

gl005.anomalies (incident lifecycle events)

gl005.explainability (attribution payloads / references)

gl005.reports (report metadata)

## 12.5 Reliability and latency targets (engineering requirements)

End-to-end alert latency target: ≤ 2 seconds (configurable).

CQI update cadence: 1–5 seconds in RUN mode (configurable).

SSE stream availability: ≥ 99.9% for production deployments (site-dependent).

Graceful degradation: if ML model unavailable, continue with rule-based scoring and explicitly flag reduced capability.

# 13. AI/ML Design (Models, Features, Training, and Governance)

## 13.1 Recommended modeling strategy (hybrid)

Use a hybrid design: physics-informed feature computation + ML for pattern recognition and residual detection. This approach improves generalization across units and fuels, and supports explainability.

Physics layer: compute AFR, λ/φ estimates, O₂-corrected emissions, stability indices, mode flags.

Statistical layer: rolling statistics, change-point detectors, control-chart metrics.

ML layer: multivariate anomaly score and/or CQI calibration model; separate models per operating mode/load bin.

Reasoning layer: map outputs to incident types and recommended checks; produce narratives.

## 13.2 Feature engineering (minimum set)

Raw signals (flows, O₂, CO, NOₓ, flame intensity, statuses) with quality flags.

Ratios: air/fuel, fuel per burner, air per burner, analyzer correlations.

Derived combustion proxies: λ/φ estimate, excess air proxy from O₂, emissions corrected to reference O₂.

Dynamics: rolling mean, rolling std, first derivative, short-term slope, step-change indicators.

Mode-aware features: one-hot operating mode, time-since-startup, time-in-run, number of burners in service.

Consistency residuals: deviation from expected AFR-vs-load curve; deviation between redundant sensors if present.

## 13.3 Candidate model families (choose per site constraints)

| Model family | When/why to use |
| --- | --- |
| Tree-based models (XGBoost/LightGBM) | Fast, explainable with SHAP, good for tabular features and CQI component modeling. |
| Isolation Forest / One-Class SVM | Baseline unsupervised anomaly detection; works well with engineered features. |
| Autoencoder (dense or temporal) | Learns normal patterns; anomaly score from reconstruction error; can be mode-specific. |
| Temporal CNN / LSTM / Transformer | Learns sequence patterns; supports attention maps; higher complexity but strong for transient detection. |
| Rule engine | Deterministic safety/mode/envelope logic; provides guaranteed coverage and interpretability. |

## 13.4 Training data and labeling

Data sources for training and evaluation:

Historian time-series for MVSS + recommended signals (≥ 3–12 months preferred).

DCS/BMS/SIS event logs: trips, alarms, state transitions, bypass events.

Maintenance records (CMMS) for analyzer calibration, burner maintenance, fan/damper repairs.

Operator logs / shift notes (if available) for contextual labeling.

Labeling strategy (practical approach):

Start unsupervised: learn normal behavior per mode; detect outliers; review top events with SMEs.

Create a labeled incident library: map historical events to taxonomy (Section 9.1).

Use weak supervision: derive labels from known alarms/trips plus engineered rules; then SME validates a subset.

Maintain a gold set for regression testing across versions.

## 13.5 Model evaluation and acceptance (ML-specific)

Backtest on unseen time periods (temporal split) to avoid leakage.

Evaluate per operating mode and load band (models often fail in low-load and transitions).

Report: precision/recall per event type, false positives/day, lead time, and explanation quality (SME rating).

Calibration of confidence scores (reliability curves) so operators can trust severity.

Stress test against sensor dropouts and invalid analyzer states.

## 13.6 Drift detection and lifecycle governance

Monitor input drift: changes in distributions of key features (O₂, AFR, flame intensity) and data quality.

Monitor concept drift: degradation in alert precision/recall and CQI stability.

Trigger workflows: retraining, parameter retuning, or instrumentation investigation.

Version everything: model, configuration (tag mapping and thresholds), and training dataset snapshots.

Approval gates: combustion SME + safety engineer sign-off for any material logic change affecting alerts.

# 14. Operator & Engineer Experience (UI/UX Requirements)

GL-005 is only valuable if operators and engineers can rapidly interpret outputs. The UI/UX must be designed for OT environments: clarity, low cognitive load, and traceable evidence.

## 14.1 Core screens / views

| View | Purpose |
| --- | --- |
| Live CQI Dashboard | CQI_total + component breakdown; last 15–60 minutes trend; operating mode and data confidence. |
| Incident Feed | Chronological list of active/recent incidents with severity, confidence, and quick summary. |
| Incident Detail | Evidence trends, top drivers (SHAP/LIME), attention map, hypotheses, and recommended checks. |
| Safety Compliance Panel | Bypass statuses, recent interlock demands/trips, mode anomalies, and data integrity for safety tags. |
| Reports | Shift/day/week summary: CQI distribution, top recurring issues, emissions excursions, maintenance suggestions. |
| Feedback/Annotation | Operator/engineer can label “false alarm”, “confirmed”, add notes; feeds model improvement loop. |

## 14.2 Alerting rules (human factors)

Integrate with existing alarm philosophy: do not create competing alarm floods.

Use consistent severity mapping (e.g., S1 informational, S2 warning, S3 urgent, S4 critical).

Include actionable next steps and references to relevant SOPs/engineering documents.

Provide “why” with every alert (top drivers) and “what changed” (signal deltas).

Offer acknowledgment and suppression mechanisms consistent with site policy (note: suppression must not hide safety boundary alerts).

# 15. Climate Intelligence Outputs (Emissions and Carbon Performance)

GL-005 provides high-frequency combustion diagnostics that can materially improve emissions performance. The Climate Intelligence workstream converts operational signals into auditable emissions and intensity metrics.

## 15.1 Required climate-related inputs

Fuel type and emission factor (kg CO₂ per unit fuel) — site-approved and version-controlled.

Fuel lower heating value (LHV) and/or composition if available (gas chromatograph, ultimate analysis).

Production/load denominator for intensity metrics (e.g., steam flow, MW, product throughput) — recommended.

## 15.2 Emissions calculations (examples)

CO₂ from fuel flow (typical approach):

CO₂_rate = Fuel_flow × EF_CO₂

Where EF_CO₂ is an approved emission factor (e.g., kg CO₂ per Nm³ of natural gas or per kg of fuel). Confirm units and standard conditions.

NOₓ/CO mass rate (if flue gas flow is known or can be approximated):

Mass_rate ≈ Concentration × Flue_gas_flow × (molecular weight / molar volume) with appropriate dry/wet corrections.

If flue gas flow is not available, GL-005 should at minimum track concentration-based KPIs and time-in-excursion metrics (ppm-hours).

## 15.3 Climate intelligence deliverables

CO₂ intensity proxy trend (kg CO₂ per unit output) and improvement attribution to CQI changes.

NOₓ and CO excursion dashboards with O₂-normalized values where required.

Monthly/quarterly reporting pack with evidence: incident summaries, corrective actions, and quantified improvements.

Opportunity identification: recurring patterns suggesting burner tuning, analyzer maintenance, or control strategy review.

# 16. Testing, Validation, and Acceptance Criteria

## 16.1 Test layers

| Test layer | What it proves |
| --- | --- |
| Unit tests | Signal conditioning, feature calculations, CQI mappings, rule engine logic. |
| Integration tests | OPC-UA ingestion, Kafka/SSE streaming, persistence, authentication. |
| Model validation | Backtests, confusion metrics, drift robustness, explainability sanity tests. |
| OT/UAT testing | Operator workflow validation, alarm hygiene checks, incident review sessions. |
| Safety verification | Read-only enforcement, fail-safe behavior, boundary monitoring correctness. |
| Performance testing | Latency under load, reconnection behavior, resource utilization on edge hardware. |

## 16.2 Acceptance criteria (minimum for production)

Data Quality Gate passed (Section 6.4).

CQI produced continuously in RUN mode with availability ≥ 99% during test period.

Anomaly detection meets site-agreed false alarm target (e.g., ≤ X nuisance alerts/day) while detecting known historical events.

Explainability delivered for ≥ 95% of incidents (with top drivers and evidence trends).

Safety boundary monitoring: bypass detection and mode anomalies validated against SIS/BMS logs with zero missed critical cases in test set.

Security and OT connectivity approved (segmentation, credentials, audit logs).

Operator/engineer sign-off after pilot (UAT) with documented feedback closure.

# 17. Deployment, Operations, and Support

## 17.1 Deployment options

| Option | Notes |
| --- | --- |
| Edge-only (recommended for OT) | All ingestion + inference + SSE within plant network. Periodic exports to enterprise systems. |
| Edge + Cloud hybrid | Edge handles ingestion and real-time alerts; cloud handles fleet analytics, long-term storage, retraining. |
| On-prem data center | Central plant/site server hosts services; suitable where OT allows and latency is acceptable. |

## 17.2 Operational requirements

Observability: metrics (latency, event rate, data quality), logs, tracing.

Health endpoints and heartbeats; alarms for connector disconnects and analyzer invalid states.

Backup/restore for configuration and incident database; retention policy for raw and derived data.

Runbooks for common failures: OPC-UA disconnect, analyzer invalid, model service crash, storage full.

Change control: configuration and model updates require approval and rollback plan.

## 17.3 Model/config update governance

All updates are versioned and deployed via CI/CD with approvals (AI lead + combustion SME + safety engineer).

Blue/green or canary deployment for model updates where feasible.

Automatic rollback on KPI regression (nuisance alarms spike, CQI instability, latency breach).

Maintain a “known-good” rule-based baseline as a fallback.

# 18. Workstreams and What Each Team Must Deliver

This section is the execution checklist. Each workstream must produce tangible deliverables that can be reviewed and signed off. Where possible, deliverables should be treated as version-controlled artifacts (Git, registry, or controlled document repository).

## 18.1 AI/ML Workstream

Define the feature library (physics + statistical + mode features) with unit tests.

Select model approach per site constraints (tree/autoencoder/transformer) and document rationale.

Build training dataset pipeline (from canonical data contract) and labeling process (incident library).

Train baseline models per operating mode and validate against historical events.

Implement explainability: SHAP (global + local), LIME fallback, and time-series attributions/attention maps.

Implement confidence estimation and calibration; define severity mapping logic.

Publish model cards: purpose, inputs, limitations, training data period, evaluation metrics.

Integrate drift monitoring and retraining triggers; define retraining cadence policy.

Deliver inference artifacts (model files, parameters) into the model registry with versioning.

## 18.2 Data Engineering Workstream

Deliver site tag map: source tags → canonical names/units; include quality code mapping.

Implement ingestion pipelines (OPC-UA to normalized stream) with buffering and replay.

Time alignment and resampling strategy; manage analyzer delay compensation.

Data quality monitoring dashboards and automated Data Quality Gate (Section 6.4).

Maintain time-series storage and incident storage with retention policies.

Provide curated training datasets (time ranges, asset IDs, mode filters) to AI/ML.

Implement schema versioning and backward compatibility (Kafka schema registry if used).

## 18.3 Software Engineering Workstream

Implement runtime services: connector orchestration, CQI/anomaly engine, incident lifecycle, explainability service integration.

Expose APIs: REST for pull + SSE for streaming; implement authentication and role-based access control (RBAC).

Implement Kafka producers/consumers if required; ensure idempotent event handling.

Build UI dashboards (or integrate into existing HMI/portal) with live CQI, incidents, explainability panels, and reports.

Implement audit logging, configuration management, and secure secrets handling.

Create deployment artifacts (containers/helm charts), health checks, and runbooks.

Implement observability (metrics/logs/traces) and alerting for service health.

## 18.4 Controls/OT Engineering Workstream

Confirm tag availability, scan rates, and units; coordinate with DCS/PLC/SIS owners.

Provide operating mode definitions and BMS state machine mapping (purge/ignite/run/trip).

Validate that integrations are read-only and comply with site OT policies.

Validate time synchronization (NTP/PTP) between data sources and GL-005 runtime.

Define alarm routing and integration points (DCS alarm summary, operator display, historian).

Support commissioning: compare GL-005 outputs to operator observations and existing alarms.

## 18.5 Combustion & Thermal Engineering Workstream

Define CQI targets/bands by load and fuel type (O₂ preferred band, CO/NOₓ targets, stability thresholds).

Define anomaly taxonomy mapping to physical root causes and recommended checks; maintain knowledge base.

Validate derived combustion metrics (λ/φ proxies, emissions normalization) and confirm engineering correctness.

Participate in labeled incident review sessions; rate explanation usefulness and correctness.

Provide tuning guidance for nuisance alarm reduction without masking real events.

## 18.6 Safety Engineering Workstream (IEC 61511 / SIL 2 boundary)

Author Safety Boundary Requirements Specification (SBRS) for what GL-005 monitors and how it reports.

Perform hazard review to confirm advisory-only design does not alter risk credit or introduce hazards.

Define safety-critical messaging rules and escalation paths for bypass/trip-related events.

Validate that GL-005 cannot write to SIS/BMS/DCS outputs (technical + procedural controls).

Approve validation evidence and audit trail design; participate in commissioning sign-off.

## 18.7 Cybersecurity / OT Security Workstream

Design OT network zoning and access control (DMZ, firewall rules, one-way where required).

Credential management: least privilege, rotation, certificate-based OPC-UA where possible.

Hardening: OS/container baselines, patching strategy, vulnerability scanning.

Logging/monitoring integration with SOC/OT monitoring tools.

Threat modeling for data ingestion and streaming endpoints; secure SSE/REST via TLS and auth.

## 18.8 Climate Intelligence Workstream

Define approved emission factors and accounting rules (units, standard conditions, reporting cadence).

Build emissions/intensity dashboards and reporting packs linked to CQI and incidents.

Quantify emissions reductions attributable to detected/tuned improvements (before/after analyses).

Align with corporate ESG/regulatory reporting processes and audit requirements.

## 18.9 QA and Validation Workstream

Create end-to-end test plan including OT integration, model performance, and UX workflows.

Build regression test suite from labeled incident library and gold datasets.

Conduct performance/latency tests under expected tag volume and event rates.

Manage UAT sessions with operators/engineers; track and close findings.

Define go-live checklist and post-go-live monitoring plan.

## 18.10 RACI Summary (who owns what)

Legend: R = Responsible (does the work) | A = Accountable (sign-off) | C = Consulted | I = Informed

| Task / Deliverable | PP | ML | DE | SE | OT | CE | SAF | SEC | CI | QA |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Site tag map + units + mode mapping | A | C | R | C | R | C | C | C | I | I |
| Data Quality Gate dashboards + pass criteria | A | C | R | C | C | C | C | C | I | R |
| CQI definition (targets/weights) + parameter set | A | C | C | I | C | R | C | I | C | C |
| Anomaly taxonomy + diagnostic knowledge base | A | R | C | I | C | R | C | I | C | C |
| Model training + evaluation report + model card | C | A/R | C | I | I | C | C | I | C | R |
| Explainability (SHAP/LIME/attention) integration | C | A/R | C | R | I | C | C | I | I | R |
| OPC-UA connector + buffering/reconnect | C | I | R | A/R | C | I | I | C | I | R |
| SSE + REST API + auth/RBAC + audit logs | C | I | C | A/R | I | I | C | C | I | R |
| UI dashboards + incident workbench | A | C | I | R | C | C | C | I | C | R |
| Safety boundary requirements (SBRS) + verification | C | I | I | C | C | C | A/R | C | I | R |
| OT security zoning + hardening + credentials | C | I | C | C | C | I | C | A/R | I | C |
| Climate emissions/intensity reporting pack | A | I | C | C | I | C | I | I | A/R | C |
| End-to-end test plan + UAT + go-live checklist | A | C | C | C | C | C | C | C | C | R |
| Deployment artifacts + runbooks + on-call process | A | I | C | R | C | I | C | C | I | R |

# 19. Proposed Timeline and Milestones (target: Q2 2026)

Exact dates depend on site readiness. The timeline below is a typical path to a production-grade deployment by Q2 2026.

| Milestone | Definition of done |
| --- | --- |
| M0 — Kickoff & scope lock | Confirm asset list, stakeholders, success metrics, and safety boundaries. |
| M1 — Data readiness complete | Tag map finalized; ingestion live; Data Quality Gate passed on historical + live streams. |
| M2 — CQI baseline + rule diagnostics | Physics-based CQI and rule checks running in real time; initial dashboards available. |
| M3 — ML anomaly model v1 | Mode-aware anomaly detection trained and backtested; incident taxonomy operational. |
| M4 — Explainability + narratives | SHAP/LIME + attention views integrated; operator-ready summaries available. |
| M5 — Pilot/UAT complete | Operators/engineers validate; nuisance alarms tuned; acceptance criteria met. |
| M6 — Safety/cyber sign-off | SBRS, hazard review, OT security approvals complete; audit trail validated. |
| M7 — Production rollout | High availability, runbooks, monitoring, and support model in place; go-live. |

# 20. Key Risks and Mitigations

| Risk | Mitigation |
| --- | --- |
| Insufficient signal quality (bad analyzers, missing tags) | Make Data Quality Gate non-negotiable; prioritize analyzer health tags and calibration capture; add recommended sensors where ROI justified. |
| Mode mixing leads to unstable models | Implement mode-aware segmentation; ensure BMS state tags are available; exclude purge/ignite from normal model training. |
| High nuisance alarm rate reduces trust | Layered detection + hysteresis; operator feedback loop; weekly tuning reviews during pilot. |
| Safety concerns or OT governance blocks deployment | Read-only enforcement, SBRS, hazard review, and OT security zoning from day one; engage safety and OT early. |
| Model drift across seasons/fuel composition changes | Drift monitoring and periodic retraining; incorporate fuel composition metadata where available. |
| Explainability not credible to engineers | Use physics features + SHAP; provide evidence trends; run sanity checks; involve SMEs in validation. |
| Latency and reliability issues on edge hardware | Performance profiling; lightweight models where required; buffering and backpressure; HA deployment patterns. |

# Appendix A — Tag Mapping Template (site onboarding)

Use this template to onboard each unit/burner. Maintain as a version-controlled file (e.g., YAML/CSV) with approvals.

| asset_id | canonical_signal | source_system | source_tag | unit | sample_period_s | notes/quality flags |
| --- | --- | --- | --- | --- | --- | --- |
| Boiler-3/Burner-2 | fuel_flow | DCS | B3B2_FUEL_FIC.PV | Nm3/h | 1 | standard conditions; density corrected |
| Boiler-3/Burner-2 | air_flow | DCS | B3B2_AIR_FIC.PV | Nm3/h | 1 | verify flow element calibration |
| Boiler-3/Burner-2 | o2_dry | CEMS | B3_STACK_O2.PV | % | 10 | include analyzer status tag |
| Boiler-3/Burner-2 | bms_mode | BMS | B3B2_MODE | enum | 1 | Purge/Ignite/Run/Trip mapping |

# Appendix B — Incident Event JSON (example)

{
  "schema_version": "1.0",
  "incident_id": "INC-2026-04-10-0012",
  "asset_id": "Boiler-3/Burner-2",
  "event_type": "CO_SPIKE",
  "severity": "S3",
  "confidence": 0.81,
  "start_ts_utc": "2026-04-10T12:31:10Z",
  "last_update_ts_utc": "2026-04-10T12:35:10Z",
  "status": "ACTIVE",
  "cqi_impact": -12.5,
  "top_drivers": [
    {"feature": "CO_ppm", "attribution": 0.42},
    {"feature": "O2_dry_pct", "attribution": 0.31},
    {"feature": "air_fuel_ratio", "attribution": 0.14}
  ],
  "recommended_checks": [
    "Verify O2/CO analyzer status and calibration mode",
    "Inspect burner register/damper position for sticking",
    "Review recent load change and burner-to-burner balance"
  ],
  "links": {
    "trend_plot": "…",
    "explainability_panel": "…"
  }
}

# Appendix C — Glossary (selected)

| Term | Meaning |
| --- | --- |
| AFR | Air–fuel ratio. |
| λ (lambda) | Excess air ratio = AFR/AFR_stoich. |
| φ (phi) | Equivalence ratio = 1/λ. |
| CQI | Combustion Quality Index (0–100 composite score). |
| CEMS | Continuous Emissions Monitoring System. |
| BMS | Burner Management System. |
| SIS | Safety Instrumented System (IEC 61511). |
| SIF | Safety Instrumented Function. |
| SHAP | SHapley Additive exPlanations (feature attribution method). |
| LIME | Local Interpretable Model-agnostic Explanations. |
| SSE | Server-Sent Events (HTTP streaming). |

End of document.