GL-007 — FurnacePulse
FurnacePerformanceMonitor

Cross‑Functional Delivery Playbook & System Requirements Specification (SRS)

Furnace performance monitoring with NFPA 86-oriented compliance evidence, tube metal temperature tracking,
predictive maintenance, explainability (SHAP/LIME), and integrated safety documentation (LOPA/HAZOP).

| Agent ID | GL-007 |
| --- | --- |
| Codename | FURNACEPULSE |
| Agent Name | FurnacePerformanceMonitor |
| Domain | Furnaces |
| Category | Monitor |
| Complexity | Medium |
| Priority | P1 |
| Value / Impact (placeholder) | $9B (as provided) |
| Target Quarter | Q1 2026 |
| Maturity / Score (placeholder) | 96 (as provided) |
| Status | Implemented (as provided) |
| Key Inputs | Furnace temperature, fuel consumption, production output, tube temps, flame detection, draft pressure, refractory condition, operating hours |
| Key Outputs | Performance KPIs, maintenance alerts, efficiency trends, hotspot detection, compliance status, safety reports, explainability dashboards, RUL predictions |
| Integrations | Furnace controls, temperature sensors, IR cameras, OPC-UA, Kafka, CMMS |
| Document version | v1.1 |
| Prepared on | December 18, 2025 |

Audience. AI/ML, data engineering, software development, OT/controls, process/thermal engineering, safety/PSM, reliability/maintenance, climate intelligence (energy/emissions), cybersecurity/IT, and operations leadership.

Safety disclaimer. GL‑007 provides monitoring, analytics, and advisory recommendations. It must not replace or override certified protection systems (BMS/SIS/SIFs). Any compliance determination or safety decision requires qualified review using the official NFPA 86 edition and site procedures. This document is an engineering implementation guide, not a certification statement.

# Table of Contents

Word can generate an automatic table of contents from headings. In Word: References → Table of Contents → Insert/Update.

# 1. Executive Summary

GL‑007 (FurnacePulse) is a furnace performance monitoring agent designed for industrial furnace environments. It unifies high-frequency OT telemetry and enterprise maintenance records to deliver actionable performance, safety, and reliability insights. The solution is built to be auditable, explainable, and integrable with existing OT/IT stacks.

## 1.1 Primary Outcomes

Reduce energy consumption and improve thermal efficiency through continuous KPI tracking and root-cause analytics.

Prevent tube and refractory damage through early hotspot detection using tube metal temperatures (TMT) and IR thermography.

Improve maintenance effectiveness via predictive maintenance models and Remaining Useful Life (RUL) estimates integrated into CMMS.

Support NFPA 86-oriented compliance programs by generating evidence packages and visibility into safety-relevant states and overrides.

Enable trustworthy AI via SHAP/LIME explainability dashboards and model governance controls.

Provide safety workflow integration by linking alerts and evidence to HAZOP recommendations and LOPA protection layers.

## 1.2 What Success Looks Like (Acceptance Summary)

Operators can see real-time furnace KPIs, hotspot risks, and alert status with <1 minute end-to-end latency (target).

Reliability team receives RUL alerts with defined lead times and can generate CMMS work orders with supporting evidence in <5 minutes.

Safety/PSM team can pull an auditable evidence package for any event, including timelines, signals, IR images, and model explanations.

All models have documented intended use, limitations, and traceable training data ranges (model cards).

# 2. Scope, System Boundaries, and Assumptions

## 2.1 In Scope

Read-only acquisition of furnace operational telemetry via OPC‑UA (and/or secure historians) and IR camera feeds.

Streaming and batch analytics for performance KPIs, hotspot detection, and predictive maintenance.

Dashboards, reports, and evidence packages for performance, maintenance, and compliance review.

Integration with CMMS for maintenance workflows and with Kafka for scalable data transport.

## 2.2 Out of Scope (Must Not Happen)

Direct control of safety-critical actuators (fuel valves, purge valves, igniters, trip circuits).

Automatic bypassing or modification of interlocks/permissives.

Any claim of compliance certification without formal audit and qualified sign-off.

## 2.3 Key Assumptions

Plant provides a tag list and access method (OPC‑UA endpoint or historian feed) with documented units and scaling.

Tube IDs and zone mapping exist (or will be created) to interpret TMT and IR imagery spatially.

CMMS contains at least 12–24 months of maintenance history for initial RUL baselines (if available).

Safety team provides site-specific compliance checklist and evidence requirements.

# 3. Reference Architecture

GL‑007 is implemented as an OT-to-IT analytics pipeline with strong governance, traceability, and segregation of duties. A recommended architecture is shown below.

Figure 1 — GL‑007 high-level architecture (recommended).

Design rule: ML outputs are advisory and must not replace certified safety functions.

# 4. Teams, Responsibilities, and Deliverables

This section is written as a delivery contract. Each team should treat its subsection as a checklist of deliverables.

## 4.1 AI/ML Team

Define use cases, labels, and success metrics per model (hotspots, efficiency degradation, RUL).

Build and maintain ML pipelines (feature extraction, training, evaluation, registry, deployment).

Implement explainability (SHAP/LIME) and model documentation (model cards, known limitations).

Deliver inference services with confidence scoring and abstain logic.

Establish monitoring for drift, performance decay, and data quality sensitivity.

## 4.2 Data Engineering Team

Implement OPC‑UA ingestion, time alignment, and store-and-forward buffering at the edge.

Design Kafka topics, schemas, retention, replay, and access controls.

Build TSDB + data lake + feature store; enforce lineage and dataset versioning.

Implement data quality flags, drift detection, and automated alerts on missing/invalid data.

Deliver a master tag registry and asset hierarchy mapping (furnace → zones → burners → tubes).

## 4.3 Software Development Team

Build KPI engine, alert orchestration, evidence packaging, and reporting services.

Build dashboards: KPIs, efficiency, hotspots, compliance status, explainability panels.

Implement CMMS integration (work order suggestion/creation) and notification channels.

Implement RBAC, audit logging, and secure APIs.

Deliver operational tooling: observability, configuration management, CI/CD.

## 4.4 OT / Controls Engineering Team

Validate tag semantics, scaling, and signal quality (including flame detector and BMS states).

Provide sequence-of-operations reference and permissive/interlock lists for evidence mapping.

Ensure read-only boundaries and OT cyber posture for gateways.

Support sensor placement documentation (TMT sensors, IR camera FOV mapping).

Run commissioning tests to verify correctness of real-time values and event timelines.

## 4.5 Process / Thermal Engineering Team

Define KPI formulas and baselines (efficiency vs load, excess air targets, stack temperature limits).

Define safe operating envelopes: TMT limits by tube service/material, draft limits, refractory heat loss thresholds.

Provide physical sanity checks for ML outputs and define alarm thresholds/tier logic.

Validate IR interpretation rules and TMT clustering logic.

Approve thermal calculation basis and sign off on reporting definitions.

## 4.6 Safety / PSM Engineering Team

Translate NFPA 86 and site standards into a measurable checklist and required evidence set.

Define hazard register linkage model (HAZOP/LOPA IDs, safeguards, IPL health indicators).

Approve alert taxonomy for safety-significant conditions and escalation workflow.

Define retention and audit requirements for evidence packages.

Approve change-control and sign-off gates for model updates and threshold changes.

## 4.7 Reliability / Maintenance Engineering Team

Define failure modes, maintenance triggers, and target lead times for alerts.

Curate CMMS history and asset metadata required for RUL models and work order templates.

Validate alert precision requirements and acceptable false alarm rates.

Own response playbooks and continuous improvement loop (post-alert review).

## 4.8 Climate Intelligence Team

Define fuel-to-emissions calculations and reporting boundaries (CO₂ and intensity metrics).

Validate energy intensity metrics (fuel/ton product, CO₂/ton) and baseline comparison logic.

Identify optimization levers and integrate them into advisory recommendations.

## 4.9 Cybersecurity / IT Team

Design OT/IT segmentation and certificate management for OPC‑UA and service-to-service encryption.

Implement IAM/RBAC, secrets management, vulnerability management, and incident response integration.

Approve deployment patterns and monitor compliance with site cyber controls.

# 5. Data Requirements and Tag Dictionary

## 5.1 Minimum Required Signals

The following signal families are mandatory (provided by the project definition). Each must include engineering units, sampling rate, quality flags, and asset mapping.

| Signal Family | Examples / Subsignals | Sampling Target | Units | Typical Source |
| --- | --- | --- | --- | --- |
| Furnace temperatures | Zone thermocouples, bridgewall temp, flue gas temps | 1–10s (typical) | °C/°F | DCS/PLC |
| Fuel consumption | Fuel flow, totalized fuel, fuel pressure/temperature | 1–10s | Nm³/h, kg/h, MMBtu/h | Flowmeters/DCS |
| Production output | Throughput, line speed, load, duty indicator | 10–60s | t/h or unit-specific | MES/DCS |
| Tube metal temperatures (TMT) | Per tube/pass skin temps | 1–10s (prefer), or 1min | °C/°F | TMT system/DCS |
| Flame detection | Flame present, flame quality, scanner health | 1s or event-driven | Boolean/enum | BMS |
| Draft pressure | Furnace/stack draft | 1–10s | Pa / inH₂O | DP transmitters |
| Refractory condition | IR skin temp, hot-spot maps, inspection findings | IR: 1–5s; inspections: event-based | °C/°F + score | IR + CMMS |
| Operating hours | Run hours, cycle counts, starts/stops | Event-based + daily rollup | h / counts | DCS/CMMS |

## 5.2 Recommended Additional Signals (Strongly Suggested)

Combustion air: flow, fan speed, damper position, air temperature.

Flue gas analyzers: O₂, CO, CO₂ (and NOₓ where available).

Burner detail: per-burner fuel valve position, air register position, igniter status, BMS permissive states.

Process side: feed/product inlet/outlet temperatures, flows, pressures to estimate absorbed duty.

Ambient: temperature, humidity, barometric pressure.

Fuel quality: Wobbe index, LHV/HHV, composition (if variable).

Rotating equipment condition: vibration, motor current, bearing temps for ID/FD fans.

Operator actions/logs: mode changes, manual overrides, tuning actions.

## 5.3 Tag Registry Template (Required Fields)

The master tag registry is a formal artifact owned by Data Engineering with OT/Process validation. Minimum fields per tag:

tag_id (unique)

tag_name_canonical

source_system (PLC/DCS/BMS/IR/CMMS)

engineering_units

engineering_range_min/max

sampling_rate

asset_id mapping (furnace/zone/burner/tube)

data_type

quality_flag mapping

description/business meaning

calibration_reference

owner/team

criticality (safety/performance)

# 6. Data Quality, Governance, and Lineage

## 6.1 Quality Flags and Rules (Minimum Set)

GOOD: valid value within engineering range and sensor healthy.

BAD: out-of-range, sensor fault, invalid status, or stale value.

SUSPECT: plausible range but failed drift/stuck tests, or inconsistent with correlated signals.

MISSING: no value received within expected time window.

## 6.2 Time Alignment Requirements

All raw points retain original timestamp + gateway receive timestamp.

Canonical analytic time base defined per use case (e.g., 5s for hotspots, 1min for KPI trends).

Resampling uses aggregation functions with explicit rules (mean, median, last-good, min/max).

Data latency and completeness metrics are computed continuously and surfaced in dashboards.

## 6.3 Governance and Audit

Every KPI and alert must be traceable to: tag versions, calculation code version, model version, and thresholds used.

All configuration changes (thresholds, model promotions, tag mappings) require change-control with approvers (Safety + Process + Ops).

Evidence packages are immutable once generated; retain per compliance policy.

# 7. System Requirements (SRS) — Functional Requirements

Requirements are written in testable form. Each requirement includes an acceptance criterion. Teams should map these to backlog items and test cases.

| Req ID | Name | Requirement Statement | Acceptance Criteria |
| --- | --- | --- | --- |
| FR-001 | Telemetry Ingestion | System shall ingest OT telemetry for all required signals via OPC‑UA (or approved historian feed) in read-only mode. | Demonstrate live ingestion for each mandatory signal family; verify no write capabilities are enabled. |
| FR-002 | Time Synchronization | System shall preserve source timestamps and provide a canonical aligned time series per analytic time base. | For a defined test window, aligned series must match raw source within agreed tolerance; timestamp provenance must be visible. |
| FR-003 | KPI Computation | System shall compute and store performance KPIs (efficiency, SFC, draft stability, etc.) with auditable formulas. | Given a test dataset, KPI outputs match reference calculations (Process Eng) within tolerance; formulas are documented. |
| FR-004 | Hotspot Detection | System shall detect TMT/IR hotspots and generate tiered alerts with evidence snapshots. | Inject simulated or historical hotspot events; system triggers correct tier and stores evidence package. |
| FR-005 | RUL Prediction | System shall provide RUL predictions (where data supports) with confidence bounds and recommended actions. | Backtest on historical failures; demonstrate lead time and performance metrics agreed with Reliability. |
| FR-006 | Explainability | System shall provide local and global model explanations (SHAP/LIME) for every ML-driven alert or prediction. | For each inference, UI/API returns top drivers + directionality + confidence; model card exists for each deployed version. |
| FR-007 | Compliance Evidence | System shall generate NFPA 86-oriented evidence packages and compliance status views based on site checklist. | Safety team validates that evidence package includes required signals/logs for a sample set of events and audits. |
| FR-008 | LOPA/HAZOP Linkage | System shall allow linking alerts and evidence to HAZOP nodes and LOPA scenarios/IPLs. | Demonstrate that each safety-significant alert can be associated with hazard scenario IDs and reported. |
| FR-009 | CMMS Integration | System shall integrate with CMMS to create or recommend work orders with attached evidence. | Given a triggered alert, user can generate a draft work order with asset ID, recommended action, and evidence attachments. |
| FR-010 | Audit Logging | System shall log user actions (acknowledgements, threshold changes, model promotions) in an immutable audit trail. | Audit log shows who/what/when for each action and is exportable for compliance review. |

# 8. System Requirements (SRS) — Non‑Functional Requirements

| NFR ID | Name | Requirement |
| --- | --- | --- |
| NFR-001 | Safety posture | Advisory only; read-only OT integration; no safety function replacement; conservative degradation under uncertainty. |
| NFR-002 | Latency | Hotspot detection path: seconds–1 minute (target). KPI dashboard refresh: ≤1 minute (target). |
| NFR-003 | Availability | Monitoring services target ≥99.5% availability; define maintenance windows and failover strategy. |
| NFR-004 | Data retention | Raw OT data retention and evidence retention per policy; minimum recommended: 12 months raw + 3–7 years evidence. |
| NFR-005 | Security | RBAC, least privilege, encryption in transit, certificate-based OPC‑UA, secrets management, OT/IT segmentation. |
| NFR-006 | Traceability | Every KPI/alert is reproducible from stored inputs, versions, and thresholds; evidence packages immutable. |
| NFR-007 | Explainability | Local explanations required for each ML inference; global summaries required per model version. |
| NFR-008 | Change control | Model updates and threshold changes require approval workflow (Safety + Process + Ops). |

# 9. Analytics, Mathematics, and Thermal Requirements

## 9.1 Required Calculations (Auditable)

Fuel energy input: based on mass/volumetric flow and LHV/HHV with documented conversion assumptions.

Energy intensity: fuel per unit production; include product normalization method.

Draft stability: variance and control effort metrics on draft pressure.

Hotspot metrics: max TMT, rate-of-rise, time-above-threshold, spatial clustering index.

Refractory loss proxy: skin temperature-based heat loss estimate (requires calibration) and/or baseline comparison.

## 9.2 Example Formulas (Illustrative; Must be Validated per Site)

Fuel Input (kW) = m_dot_fuel (kg/s) × LHV (kJ/kg) / 1,000

Specific Fuel Consumption (SFC) = Fuel Input / Production Output

CO₂ Emissions (kg/h) = Fuel Energy Input (GJ/h) × EF_CO2 (kg/GJ) 
  (EF_CO2 depends on fuel type/composition; use site-approved factors)

Excess Air Proxy (approx., fuel-dependent):
  Excess Air (%) ≈ 100 × O2_dry / (21 − O2_dry)
  (Use only with correct fuel basis and validated analyzer conditions)

Stack Loss Proxy (requires flue flow estimate or proxy):
  Q_stack ≈ m_dot_flue × Cp_flue × (T_stack − T_ambient)

## 9.3 Thermal Instrumentation Requirements (Minimum)

TMT sensors: defined attachment method, calibration record, and response time; tube ID mapping mandatory.

IR cameras: calibration and emissivity settings documented; camera-to-furnace geometry mapping maintained; image timestamping synchronized.

Draft pressure: transmitter range and tap location documented; verify zeroing and drift checks.

Fuel metering: flowmeter type, correction (pressure/temperature), and totalizer consistency documented.

# 10. Safety, NFPA 86 Evidence, and Risk Integration

## 10.1 NFPA 86-Oriented Checklist Mapping (Pattern)

GL‑007 must implement a configurable checklist and evidence mapping layer. The checklist is owned by Safety/PSM. Typical checklist categories (non-exhaustive):

Purge and startup sequence evidence (states, timers, permissives satisfied).

Flame safeguard device status and diagnostics per burner.

Interlock/permissive health and override visibility (forced I/O, bypasses, manual modes).

Fuel/air ratio boundaries and unsafe condition indicators.

Alarm and trip history with immutable timestamps.

Proof-test and maintenance status for safety-relevant instrumentation (via CMMS).

## 10.2 LOPA and IPL Health Monitoring

Create a Protection Layer Register with unique IDs for each IPL (BMS, alarms, relief devices, operator response layers).

Link telemetry that indicates degradation of an IPL (e.g., flame scanner fault rate, proof-test overdue) to risk views.

Provide ‘IPL health’ dashboard with overdue tests, overrides, and repeated demands.

## 10.3 HAZOP Recommendation Tracking

Maintain mapping of HAZOP recommendations to monitoring logic, thresholds, and evidence outputs.

Expose recommendation closure status and MOC references.

Support incident investigation workflow with event reconstruction timelines.

# 11. Alert Taxonomy and Response Playbooks (Required)

All alerts must have: severity, detection logic, confidence score, recommended actions, owner role, and required acknowledgement.

| Alert ID | Name | Trigger (summary) | Primary Owner | Example Response |
| --- | --- | --- | --- | --- |
| A-001 | Hotspot — Advisory | TMT approaching threshold; IR suggests emerging hotspot | Operator/Process Eng | Increase monitoring, verify burners, consider load adjustment; create investigation note. |
| A-002 | Hotspot — Warning | Sustained TMT exceedance or accelerating rate-of-rise | Operator + Reliability | Execute site playbook: burner tune check, confirm tube mapping, schedule inspection, consider controlled shutdown if needed. |
| A-003 | Hotspot — Urgent | High-confidence hotspot with risk to tube integrity | Ops + Safety | Immediate escalation per site procedure; confirm safety systems; consider shutdown; generate evidence package. |
| A-010 | Efficiency Degradation | Efficiency or SFC deviates from baseline beyond threshold | Process + Climate | Investigate excess air, stack temp, draft, refractory; recommend tuning and heat loss mitigation. |
| A-020 | Draft Instability | Draft variance/effort indicates control issue | OT/Controls | Inspect dampers/fans, check transmitter; review control tuning. |
| A-030 | Sensor Drift/Stuck | Signal fails drift/stuck tests | OT + Data Eng | Flag analytic confidence; schedule calibration; update tag registry. |

# 12. Interfaces and Integrations

## 12.1 OT Interfaces

OPC‑UA: certificate-based authentication; whitelisted nodes; read-only credentials.

IR feeds: store raw images/frames in object storage with metadata; derived hotspot maps stored as artifacts.

Edge gateway: local buffering for ≥24h recommended to handle network partitions.

## 12.2 Kafka Topic Design (Recommended)

Topic naming: gl007.<site>.<furnace_id>.telemetry, gl007.<site>.<furnace_id>.events, gl007.models.inference, gl007.alerts.

Schema registry: enforce backward-compatible schema evolution.

Retention: telemetry per policy; events/alerts longer retention for investigations.

## 12.3 CMMS Integration

Asset hierarchy mapping must match CMMS equipment IDs.

Work order payload includes: asset ID, alert ID, recommended actions, urgency, attachments (plots/IR/SHAP).

Closure feedback loop: work order outcomes feed model retraining and false alarm reduction.

# 13. Testing, Validation, and Commissioning

## 13.1 Commissioning Tests (Suggested Minimum)

Signal correctness: compare live values vs DCS/HMI for each key signal.

Event timeline correctness: verify alarm/trip timestamps and sequence fidelity.

Hotspot injection test: replay historical event or simulate thresholds to verify alert tiers and evidence capture.

CMMS integration test: generate a work order and verify attachments and metadata.

Security test: confirm read-only OT access and RBAC enforcement.

## 13.2 Model Validation Gates

Model review board includes AI/ML, Process/Thermal, Reliability, Safety/PSM.

Models must pass: offline metrics, drift sensitivity tests, and explainability plausibility checks.

A/B or shadow deployment required before full production alerts for safety-significant use cases.

# 14. Operations, Monitoring, and Continuous Improvement

Monitor data pipelines: lag, drop rates, missingness, schema errors.

Monitor analytics: alert volumes, false positives, user acknowledgements, response times.

Monitor models: drift, performance on recent data, explanation stability.

Run monthly review: top loss drivers, hotspot events, maintenance outcomes, model improvement backlog.

# 15. RACI Matrix (Summary)

R = Responsible, A = Accountable, C = Consulted, I = Informed.

| Workstream | R | A | C | I |
| --- | --- | --- | --- | --- |
| Tag registry & asset mapping | Data Eng | OT/Controls | Process | AI/ML, SW, Safety |
| Edge gateway deployment | OT/Controls | Cyber/IT | Data Eng | Ops |
| Kafka/Storage platform | Data Eng | IT Platform | Cyber | AI/ML, SW |
| KPI definitions & baselines | Process/Thermal | Operations | Climate, Safety | Data Eng, SW |
| Hotspot detection thresholds | Process/Thermal | Safety/PSM | AI/ML, OT | Ops |
| RUL alerts & CMMS workflow | Reliability | Operations | AI/ML, SW | Safety |
| Model promotion/change control | AI/ML | Safety/PSM | Process, Ops | All |
| Compliance evidence reports | Safety/PSM | Plant Mgmt | SW, OT | All |

# 16. Q1 2026 Delivery Plan (Illustrative)

Weeks 1–2: Finalize requirements, tag registry, architecture approval, safety boundary definition, checklist draft.

Weeks 3–5: Deploy OPC‑UA gateway, implement Kafka + TSDB + data lake pipelines, enable data quality metrics.

Weeks 6–8: KPI engine, baseline curves, first dashboards, initial hotspot rules and evidence packages.

Weeks 9–11: ML models (anomaly + RUL), explainability dashboards, CMMS integration, alert orchestration.

Weeks 12–13: Commissioning, validation, safety review, documentation completion, production rollout.

# Appendix A — Glossary

| Term | Definition |
| --- | --- |
| BMS | Burner Management System |
| CMMS | Computerized Maintenance Management System |
| HAZOP | Hazard and Operability Study |
| LOPA | Layer of Protection Analysis |
| NFPA 86 | Standard for Ovens and Furnaces (site must use official edition) |
| OPC‑UA | Open Platform Communications Unified Architecture |
| RUL | Remaining Useful Life |
| SHAP | SHapley Additive exPlanations |
| LIME | Local Interpretable Model‑agnostic Explanations |
| TMT | Tube Metal Temperature |
| TSDB | Time‑Series Database |

# Appendix B — Example Kafka Telemetry Message (Simplified)

{
  "furnace_id": "FURNACE_01",
  "timestamp_utc": "2026-01-15T10:05:00Z",
  "signals": {
    "fuel_flow_nm3h": {"value": 1520.4, "quality": "GOOD"},
    "zone1_temp_c": {"value": 1025.2, "quality": "GOOD"},
    "draft_pa": {"value": -18.3, "quality": "GOOD"},
    "tmt_tube_12_c": {"value": 575.0, "quality": "GOOD"},
    "flame_burner_03": {"value": 1, "quality": "GOOD"}
  },
  "source": {"opcua_server": "DCS01", "gateway": "EDGE-A1", "schema_version": "1.0"}
}

# Appendix C — Evidence Package Contents (Recommended)

Event summary and affected assets.

Trend snapshots (fuel, temps, draft, flame signals) with time window.

IR snapshots and hotspot annotations (if applicable).

Model outputs + SHAP/LIME explanation + confidence.

User acknowledgements and actions taken.

Linked CMMS work order(s) and closure notes.

Related HAZOP/LOPA references and protection layer notes.