GL-022 — SUPERHEAT-CTRL
Superheater Control Agent Blueprint

Steam Systems | Controller | P2 | Medium

Status: Implemented | Target Release: Q3 2026 | Maturity: 95
Budget Envelope: $5B (program-level)
Document Version: 1.1 | Date: 2025-12-26

# Document control

This document defines what each team must build, validate, and operate for GL-022 (SUPERHEAT-CTRL). It is written to be executable as a delivery plan and a technical specification.

Scope of applicability: Superheater temperature control via spray attemperation (desuperheater) for steam generation systems (boilers/HRSGs), including tube metal temperature (TMT) monitoring, creep life assessment, thermal shock protection, and compliance reporting.

Key design principle: Zero-hallucination deterministic calculations for all numeric outputs. Natural-language narratives must be traceable to data and computations with verifiable provenance hashes.

| Version | Date | Author/Owner | Notes |
| --- | --- | --- | --- |
| 1.1 | 2025-12-26 | GL Program / Steam Systems | Added team playbooks; refined thermal/math sections |

# Table of contents

1. Executive summary

2. Agent definition and success criteria

3. System boundary and operating assumptions

4. Cross-team responsibilities (RACI) and team playbooks

5. Data requirements and data engineering plan

6. Deterministic thermodynamics engine (IAPWS-IF97)

7. Spray water optimization via enthalpy balance

8. Control strategy: cascade + feedforward PID with anti-windup

9. Tube metal temperature monitoring and creep life assessment (API 530-aligned)

10. Thermal shock protection and constraints

11. Safety, interlocks, and compliance (ASME Section I / B31.1 / API 530)

12. Explainability, uncertainty quantification, and zero-hallucination UX

13. Provenance, audit logging, and reproducibility

14. Integration architecture (DCS/PLC, OPC-UA, Kafka, GraphQL, SCADA, CMMS)

15. Testing, validation, and acceptance

16. Deployment, operations, and monitoring

17. Climate intelligence and efficiency reporting

18. Appendices (math, templates, payloads, glossary)

# 1. Executive summary

GL-022 (SUPERHEAT-CTRL) is a SuperheaterControlAgent that optimizes superheater outlet steam temperature using spray attemperation (desuperheater) while protecting tube metal temperatures and managing creep/thermal shock risk. It combines deterministic IAPWS-IF97 thermodynamic property calculations, enthalpy-balance spray optimization, and industrial control logic (cascade/feedforward PID with anti-windup). The agent produces both control outputs and engineering-grade diagnostics (tube stress, creep life, thermal shock risk), plus explainability and provenance artifacts suitable for audit and compliance workflows.

Primary outcomes

Maintain superheater outlet temperature at setpoint with minimal overshoot and oscillation under load changes.

Minimize spray water consumption while respecting temperature, stress, and safety constraints (enthalpy-based optimization).

Continuously monitor tube metal temperatures (TMT) and estimate creep life consumption; alert and constrain operation as needed.

Detect and prevent thermal shock events caused by rapid temperature transients or spray step-changes.

Provide deterministic, reproducible calculations and human-readable explanations with complete provenance tracking.

Key interfaces

Inputs: steam inlet/outlet temperatures, pressures, flows; TMTs; spray rate; spray water quality; process demand setpoints; safety interlocks; valve positions.

Outputs: optimal spray setpoint; PID outputs; temperature predictions; tube stress + creep life; safety status; thermal shock risk; efficiency metrics; explainability reports; uncertainty quantification; natural language summary; provenance hash.

Integrations: DCS/PLC, superheater instrumentation, spray control valves, tube temp sensors, CMMS, OPC-UA, Kafka, GraphQL, SCADA.

# 2. Agent definition and success criteria

Agent record

| Agent ID | GL-022 |
| --- | --- |
| Agent code name | SUPERHEAT-CTRL |
| Class | SuperheaterControlAgent |
| Domain | Steam Systems |
| Category | Controller |
| Priority | P2 (Medium) |
| Program budget envelope | $5B (program-level placeholder) |
| Planned quarter | Q3 2026 |
| Maturity score | 95 |
| Status | Implemented |

Definition of done (engineering + product)

| Area | Acceptance criteria |
| --- | --- |
| Temperature control performance | Outlet steam temperature maintained within plant-defined band (e.g., ±5°C steady-state) with bounded overshoot after step/load changes; tuning documented. |
| Spray optimization | Spray water setpoint computed deterministically via enthalpy balance; achieves measurable reduction in spray flow for same temperature control (baseline comparison). |
| Tube protection | TMT limits and ramp-rate constraints enforced; creep life assessment runs continuously; alarms and constraints integrate with DCS/SCADA. |
| Safety compliance | Control outputs respect safety interlocks; agent never defeats or overrides SIS; compliance artifacts prepared for ASME/B31.1/API 530 review. |
| Explainability + provenance | Every numeric output has traceable inputs and calculation path; agent emits provenance hash and calculation report; natural language explanations cite exact values used. |
| Reliability | Graceful degradation on sensor loss; deterministic fallbacks; uptime and latency within control requirements. |

# 3. System boundary and operating assumptions

GL-022 operates as an advisory or supervisory control layer that computes optimal spray water setpoints and related diagnostics. It may be deployed at the edge (near DCS/PLC) for low-latency control, with centralized services for reporting, analytics, and model governance.

## 3.1 Included equipment and streams

Superheater section(s) with outlet temperature measurement(s).

Desuperheater/attemperator with spray control valve(s) and flow measurement (or inferred flow via valve characterization).

Steam inlet/outlet pressure and flow measurement for the controlled section.

Tube metal temperature sensors (thermocouples or equivalent) and/or inferred TMT via validated thermal model.

Spray water supply quality instrumentation and/or lab measurements (conductivity, pH, dissolved solids, silica, etc.).

## 3.2 Explicit non-goals / exclusions

Replacing existing Safety Instrumented System (SIS) logic or boiler protection functions.

Re-rating pressure parts or producing code-stamp engineering calculations; the agent produces decision-support artifacts for licensed engineers.

Closed-loop control of fuel/air or drum level (except as feedforward signals).

## 3.3 Operating assumptions (must be validated per site)

Sensors are calibrated and time-synchronized to within an agreed tolerance (e.g., ≤1 s skew for control signals).

Steam is single-phase superheated at the controlled outlet measurement point (no significant wetness).

Spray water injection mixes sufficiently before the controlled temperature measurement point (or mixing delay is modeled).

Valve characteristics (Cv curve, hysteresis, stiction) are known or identified and maintained.

Material grade and tube geometry required for creep/stress assessment are available from design records.

# 4. Cross-team responsibilities (RACI) and team playbooks

## 4.1 RACI matrix

RACI below is a starting point. Each site/program must finalize ownership based on organizational structure and regulatory accountabilities.

| Workstream | AI/ML | Software Dev | Data Eng | Controls Eng | Thermal/Mech Eng | Instrumentation | Safety/Compliance | Operations | CMMS/Reliability | Climate Intelligence | Cybersecurity/IT | QA/Testing |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Requirements and tag mapping | C | R | R | C | C | R | C | C | C | C | C | A |
| OPC-UA/Kafka ingestion and historian alignment | C | C | R | C | C | C | C | C | C | C | A | C |
| IAPWS-IF97 property engine (deterministic) + verification | C | R | C | C | A | C | C | C | C | C | C | C |
| Enthalpy-balance spray optimizer | C | R | C | A | A | C | C | C | C | C | C | C |
| Cascade/feedforward PID design, tuning, anti-windup | C | C | C | A | A | C | C | R | C | C | C | C |
| Thermal shock constraints and ramp-rate limits | C | C | C | A | A | C | C | R | C | C | C | C |
| TMT monitoring + sensor health | C | C | C | C | A | A | C | R | R | C | C | C |
| Creep life assessment (API 530-aligned), alerts, reporting | C | C | C | C | A | C | A | C | R | C | C | C |
| Explainability + narratives (SHAP/LIME or deterministic sensitivity) | A | R | C | C | C | C | C | R | C | C | C | C |
| Provenance hashing, audit logging, reproducibility | C | A | C | C | C | C | C | C | C | C | R | C |
| Safety review, MOC, compliance sign-off artifacts | C | C | C | C | C | C | A | R | C | C | C | C |
| Deployment (edge/runtime), monitoring, incident response | C | A | C | C | C | C | C | R | C | C | R | C |

Legend: R = Responsible; A = Accountable; C = Consulted; I = Informed.

## 4.2 Team playbooks (what each team must do)

### AI/ML team

Define which components are strictly deterministic (required for numeric control outputs) and which may be predictive/ML (optional) without affecting safety.

If ML is used (e.g., temperature prediction, sensor validation, anomaly detection), produce: feature list, training dataset spec, model card, validation results, and SHAP/LIME explanation pipeline.

Implement 'grounded narrative generation': the natural-language layer may only reference values present in the computation record; include provenance hash in every narrative.

Design uncertainty quantification outputs and ensure they are deterministic and monotonic with input uncertainty.

Define drift monitoring and re-training governance if ML is deployed (thresholds, approvals, rollback).

### Software development team

Implement the edge runtime services (thermo engine wrapper, optimizer, controller, diagnostics) with deterministic scheduling and bounded latency.

Implement Write Gateway with authentication, interlock gating, limit checks, rate limits, and full audit logging.

Implement GraphQL read APIs and report-generation endpoints; ensure no write capability is exposed through GraphQL.

Build configuration/version management: unit-specific configs (valve curves, limits, material data, PID tuning) with immutable versioning and approvals.

Implement provenance hashing and tamper-evident logging; ensure every output record is reproducible.

### Data engineering team

Deliver tag mapping (logical name → DCS/OPC-UA tag), unit normalization, and quality flag propagation.

Stand up OPC-UA gateway and Kafka topics with strict schemas (Avro/Protobuf) and retention policies.

Ensure time synchronization across DCS, gateway, and edge compute; monitor clock drift and message delay.

Implement data quality checks (range, rate-of-change, missing data) and deterministic filtering rules with explicit reporting.

Provide historical data extracts for tuning/validation and offline replay testing.

### Controls engineering team

Define control modes (observe-only/advisory/supervisory/active) and operator interaction model; align with plant control philosophy.

Design and tune cascade PID structure, anti-windup, bumpless transfer, and setpoint ramping.

Validate mixing delay and measurement placement; develop dynamic model or dead-time compensation strategy if needed.

Define constraints: min superheat margin, spray limits, valve slew limits, and thermal shock ramp-rate limits (with mechanical engineering).

Execute closed-loop simulation/HIL tests and document tuning and stability margins.

### Thermal / mechanical engineering team

Provide design data: tube geometry, material grades, allowable stresses/creep curves, and TMT limits; approve creep life methodology (API 530-aligned or site-approved).

Define thermal shock limits (dT/dt, ΔT gradients) and validate against equipment design and past incidents.

Approve assumptions used in enthalpy balance (adiabatic mixing, pressure selection) and any heat-transfer/TMT inference models.

Define acceptance criteria for creep damage reporting and inspection recommendations; integrate with reliability strategy.

### Instrumentation team

Validate sensor placement and calibration for T_out, P, flow, and TMT sensors; provide calibration certificates and drift expectations.

Ensure spray flow measurement is available and reliable; if inferred, support valve characterization and ΔP measurement.

Implement sensor health diagnostics (open thermocouple detection, comms loss, stuck signal) and expose to the agent via quality flags.

Support commissioning tests for step response and time alignment verification.

### Safety / compliance team

Define governance: what the agent may write, when, and under what approvals; align with MOC process.

Review and approve safety gating logic, safe-mode behavior, and alarm philosophy.

Review compliance evidence package for ASME Section I / B31.1 / API 530 alignment; ensure documentation meets site standards.

Ensure cybersecurity requirements are met for OT integration and write capability.

### Operations team

Define operator setpoint management expectations and how GL-022 interacts with existing DCS loops.

Participate in observe-only and advisory phases; provide feedback on dashboards, explanations, and alarm usability.

Validate that constraint behaviors and safe-mode transitions are operationally acceptable.

Own day-to-day response procedures for alarms related to TMT, shock risk, and data quality.

### CMMS / reliability team

Define inspection and maintenance thresholds based on creep damage indicators and TMT exceedances.

Specify how GL-022 evidence packets map to CMMS work processes (notifications, work orders, inspection routes).

Validate that calculated hot-spot rankings align with inspection findings and refine thresholds/locations accordingly.

### Climate intelligence team

Define reporting requirements for spray water consumption, efficiency impacts, and CO₂e attribution.

Integrate GL-022 outputs into sustainability dashboards; ensure assumptions (fuel factors, boundaries) are documented.

Use GL-022 event logs (constraint activations, shock near-misses) as inputs to risk and resilience reporting where applicable.

### Cybersecurity / IT team

Approve network segmentation and identity/access management for OT write paths.

Review container/runtime hardening, patching processes, secrets management, and logging retention.

Implement monitoring for anomalous write attempts, unusual traffic, or integrity violations in audit logs.

### QA / testing team

Own test plan across unit, integration, replay, simulation/HIL, and SAT; track results to acceptance criteria.

Validate determinism claims (same inputs → same outputs) and reproducibility with stored provenance records.

Verify failure modes: missing sensors, bad quality, network loss, solver non-convergence, actuator saturation.

# 5. Data requirements and data engineering plan

GL-022 is control-grade. Data engineering must treat it as a real-time cyber-physical application (not a batch analytics job). The agent requires reliable, time-synchronized measurements with clearly defined units, ranges, and quality flags.

## 5.1 Required real-time signals (minimum set)

| Signal | Symbol | Units | Typical update | Purpose / notes |
| --- | --- | --- | --- | --- |
| Steam inlet temperature | T_in | °C | 1–5 s | Feedforward and inlet enthalpy. |
| Steam outlet temperature | T_out | °C | 1–5 s | Controlled variable (CV) for outer loop. |
| Steam inlet pressure | P_in | bar(a) or MPa | 1–5 s | Thermo properties; can use section pressure if single. |
| Steam outlet pressure | P_out | bar(a) or MPa | 1–5 s | Thermo properties; saturation/superheat margin. |
| Steam mass flow | m_s | kg/s | 1–5 s | Enthalpy balance and feedforward. |
| Spray water mass flow | m_w | kg/s | 1–5 s | Inner loop PV; mixing balance. |
| Spray valve position | u_valve | % open | 0.5–1 s | Inner loop MV feedback; valve diagnostics. |
| Tube metal temperatures (multiple points) | TMT_i | °C | 1–10 s | Creep + thermal shock protection. |
| Spray water temperature | T_w | °C | 1–30 s | Water enthalpy in mixing balance. |
| Spray water quality indicators | Chem_* | various | minutes–hours | Deposit/corrosion risk constraints. |
| Steam temperature setpoint | SP_T_out | °C | 1–5 s | Operator/optimizer setpoint. |
| Safety interlock status | SIS_state | boolean/enum | 1 s | Write gating; safe-mode triggers. |
| Mode and permissives | Mode | enum | 1 s | Auto/manual/cascade enable; operator intent. |
| Valve feedback/limits (optional) | Valve_* | various | 1–5 s | Stroke time, travel limits, diagnostics. |

## 5.2 Required static / engineering reference data (per unit)

P&IDs and equipment data sheets for superheater(s), attemperator(s), valves, and instruments.

Valve characterization curves (Cv vs. position), actuator limits, fail-safe position, stroking time, hysteresis/stiction observations.

Tube geometry (OD/ID/thickness), material grade, design/allowable stress data, and original design conditions.

Material creep-rupture data or allowable stress tables consistent with the selected creep methodology (API 530-aligned or site-approved equivalent).

TMT sensor locations (axial/circumferential position), attachment details, and calibration certificates.

DCS/SIS logic narratives relevant to superheater temperature and attemperator permissives/interlocks.

Historian tag list with engineering units and scaling; time synchronization configuration (NTP/PTP).

## 5.3 Data quality requirements

| Topic | Requirement |
| --- | --- |
| Units and scaling | All tags unit-normalized at ingestion (e.g., MPa, °C, kg/s). |
| Time alignment | Common time reference (UTC recommended). Align to control cycle with bounded skew (target ≤1 s). |
| Quality flags | Each measurement includes quality metadata (GOOD/BAD/UNCERTAIN, sensor status, comms status). |
| Missing data handling | Per-signal fallback policy: hold-last-value duration, substitution source, or safe-mode transition. |
| Outlier handling | Deterministic spike filters with explicit reporting; never silently smooth without reporting. |
| Validation ranges | Engineering min/max and rate-of-change limits; violations flagged and propagated to uncertainty. |

## 5.4 Data pipeline and schemas (OPC-UA → Kafka → services)

Recommended pattern: OPC-UA gateway publishes real-time tag updates to Kafka topics with strict schemas (Avro/Protobuf). GL-022 consumes from Kafka for control-grade latency; GraphQL exposes read APIs for UIs and external services. SCADA/DCS writes are mediated via an approved interface layer with safety gating.

Canonical event schema (example)

{
  "ts_utc": "2026-07-15T13:05:12.345Z",
  "asset_id": "UNIT-3-SH1",
  "tag": "T_OUT",
  "value": 538.2,
  "unit": "degC",
  "quality": "GOOD",
  "source": "OPCUA_GATEWAY_1",
  "sequence": 981273641,
  "meta": { "range_min": 0.0, "range_max": 650.0 }
}

## 5.5 Data retention and governance

Real-time store: retain high-resolution (1–5 s) for at least 30–90 days for tuning and incident analysis.

Historian: retain aggregated (1 min, 15 min) long-term for performance and climate reporting.

Model/config store: versioned configuration for every unit (valve curves, limits, material properties).

Access control: least-privilege; separate read vs write privileges; all write actions audited.

Data lineage: each GL-022 output record includes input tag versions, config versions, and software/model versions.

# 6. Deterministic thermodynamics engine (IAPWS-IF97)

All thermodynamic calculations for steam and water must use IAPWS-IF97 formulations. GL-022 uses these properties to perform enthalpy balance, compute mixing outcomes, and determine superheat margin relative to saturation.

## 6.1 Property functions required

h(p,T): specific enthalpy at pressure p and temperature T

T(p,h): temperature from pressure and enthalpy (needed when solving mixing equations)

T_sat(p): saturation temperature at pressure p (for superheat margin)

x(p,h) or x(p,T): vapor quality near saturation (alarm if wet steam at measurement point)

Optional diagnostics: s(p,T), ρ(p,T), cp(p,T) if needed for heat-transfer inference

## 6.2 Superheat margin requirement

Define and enforce a minimum superheat margin to avoid wet steam downstream of attemperation:

Superheat margin:
  ΔT_superheat = T_out - T_sat(P_out)

Constraint:
  ΔT_superheat ≥ ΔT_min (site-defined, e.g., 10–25°C depending on turbine/plant requirements)

If ΔT_superheat approaches ΔT_min:
  • clamp spray demand
  • raise warning/alarm
  • adjust setpoint strategy per operations

## 6.3 Determinism and verification

Determinism: identical inputs + config → identical outputs (within defined floating-point tolerance/rounding policy).

Region selection: implement IF97 region logic deterministically (Regions 1–5 + saturation).

Range checks: reject/flag inputs outside IF97 validity ranges; propagate uncertainty/quality flags.

Verification: automated tests against IF97 reference points and regression tests near region boundaries.

# 7. Spray water optimization via enthalpy balance

The optimizer computes the spray water mass-flow setpoint required to achieve a desired superheater outlet temperature at the prevailing pressure and steam flow. The core calculation is an adiabatic mixing enthalpy balance using IAPWS-IF97 properties.

## 7.1 Governing equation (adiabatic mixing)

Assumptions (engineering-validated):
• Single-phase superheated steam at inlet to attemperator mixing zone.
• Spray water injected and evaporated/mixed with negligible heat loss (adiabatic control volume).
• Outlet pressure approximately equal to measured section pressure (use P_out or best available).

Mass + energy balance:
  m_s * h_s_in  +  m_w * h_w_in  =  (m_s + m_w) * h_out

Target:
  h_target = h(P_out, T_sp)

Solve for required spray flow:
  m_w,req = m_s * (h_s_in - h_target) / (h_target - h_w_in)

Rules:
• If m_w,req < 0 → set to 0 (no spray required).
• If denominator approaches 0 or states invalid → raise diagnostic and inhibit writes.

## 7.2 Constraints and objective

Hard constraints: interlocks, valve travel, min/max spray, rate-of-change limits, minimum superheat margin, TMT limits, thermal shock limits.

Primary objective: meet T_out setpoint or safe reduced setpoint under constraints.

Secondary objective: minimize spray flow and actuator movement (reduce energy penalty and mechanical wear).

## 7.3 Outputs

m_w,ff (feedforward spray demand) from enthalpy balance.

Predicted outlet temperature T_out_pred and ΔT_superheat margin.

Constraint status and remaining margins.

Uncertainty band for m_w,ff and T_out_pred based on sensor accuracy.

# 8. Control strategy: cascade + feedforward PID with anti-windup

GL-022 implements feedforward plus cascade PID: a temperature outer loop trims around a physics-based spray demand, and a faster inner loop regulates spray flow/valve behavior.

## 8.1 Block overview

T_sp ──►[Outer PID on T_out]──► Δm_w ──┐
                                     │
                         m_w,ff ──────┼──► m_w,sp ──►[Inner PID on m_w or valve]──► u_valve
                                     │
Constraints / TMT / shock limits ─────┘

## 8.2 Anti-windup and bumpless transfer

Anti-windup required: freeze or back-calculate integrator when output is saturated or constrained.

Bumpless transfer required between AUTO/MAN and cascade enable/disable; record mode transitions in audit log.

When inhibited (interlock active or data invalid), outputs must go to safe state and integrators must not wind up.

## 8.3 Deterministic pseudocode (illustrative)

At each control cycle:
  1) Validate inputs + quality flags
  2) Compute IF97 properties; compute m_ff (enthalpy balance)
  3) Outer PID computes trim Δm (with anti-windup)
  4) Apply constraints and ramp limits → m_sp
  5) Inner PID drives valve to achieve m_sp (flow control preferred)
  6) Compute diagnostics: superheat margin, shock risk, creep metrics
  7) Emit outputs + explanation + provenance hash
  8) If write-enabled and permitted, send command via Write Gateway

# 9. Tube metal temperature monitoring and creep life assessment (API 530-aligned)

GL-022 continuously monitors tube metal temperatures (TMT) and computes creep life consumption estimates. Results are decision-support and must be reviewed by qualified engineering per site governance.

## 9.1 Inputs

Measured TMT_i at defined locations (preferred).

Steam-side pressure at the tube section (for hoop stress estimate).

Tube geometry and material grade; creep-rupture/allowable stress references.

Operating history time series; start/stop cycles for duty-cycle accounting.

## 9.2 Minimum stress + damage model

Hoop stress (thin-wall approximation):
  σ_hoop ≈ (P * D_o) / (2 * t)

Creep damage accumulation:
  Damage = Σ (Δt / t_r(T, σ))

Where t_r(T, σ) comes from material-specific creep-rupture data.

Outputs include:
  • Damage_i, Remaining life estimate, Damage rate
  • Hot-spot ranking and evidence packet for inspection planning

# 10. Thermal shock protection and constraints

Thermal shock is prevented by enforcing ramp-rate and gradient constraints using TMT and steam temperature measurements.

## 10.1 Indicators and limits

Ramp rate: d(TMT_i)/dt and d(T_out)/dt compared to engineering-defined limits.

Spatial gradient: ΔTMT across monitored locations compared to limits.

Spray command rate: d(m_w_sp)/dt and valve slew rate limited to prevent step changes.

## 10.2 Risk index and protective actions

Example risk index:
  R_shock = max_i( |dTMT_i/dt|/Limit_dTMT_dt_i , |ΔTMT_i|/Limit_ΔTMT_i )

Protective actions:
  • rate-limit spray setpoint and valve command
  • clamp spray if superheat margin is threatened
  • alarm and/or revert to safer mode per site policy

# 11. Safety, interlocks, and compliance (ASME Section I / B31.1 / API 530)

GL-022 must not compromise boiler/HRSG safety systems. It respects DCS/SIS permissives and interlocks and provides compliance-ready evidence for engineering review.

## 11.1 Safety principles

No defeat of SIS logic; GL-022 never overrides trips or protective actions.

Fail-safe behavior on bad data, comms loss, or compute health issues (site-defined).

Write gating: interlock and mode checks in a dedicated Write Gateway.

All writes and parameter changes audited with provenance hash.

## 11.2 Evidence package

Control narrative + logic diagrams and constraint logic.

IF97 verification report; tuning record; valve characterization evidence.

TMT and creep methodology basis; thresholds and approvals.

MOC record for enabling supervisory control; cybersecurity review artifacts.

FAT/SAT test results and incident response runbook.

# 12. Explainability, uncertainty quantification, and zero-hallucination UX

GL-022 outputs must be explainable and auditable. Natural-language summaries must be strictly grounded in the computed record.

## 12.1 Zero-hallucination requirements

If required inputs are missing/invalid, output 'Unavailable' with explicit reason; do not guess.

Narratives may only reference values present in the record; include timestamp and provenance hash.

Report which constraints were active and the margins to key limits.

## 12.2 Explainability mechanisms

Deterministic: equation breakdown (enthalpy balance, PID P/I/D terms, clamps).

If ML is used: SHAP/LIME explanations stored per prediction; model card and version in provenance.

## 12.3 Uncertainty quantification

Propagate sensor accuracy into uncertainty bands for m_w,ff, T_out_pred, and creep damage rate.

UQ must be deterministic and reproducible; widen bands when data quality degrades.

# 13. Provenance, audit logging, and reproducibility

Every output record must be reproducible offline using captured inputs, configuration versions, and software versions.

## 13.1 Provenance contents

Inputs (values + units + quality flags), configuration snapshot IDs, software/build IDs, IF97 version.

Intermediates (h-values, m_ff, PID terms, clamp results) and final outputs.

If ML used: model version and dataset reference.

## 13.2 Hashing requirement

Compute SHA-256 over canonical JSON of:
  { inputs, config_versions, software_versions, outputs, intermediates }

Canonicalization must enforce stable key ordering and numeric formatting.

# 14. Integration architecture (DCS/PLC, OPC-UA, Kafka, GraphQL, SCADA, CMMS)

Recommended architecture separates control-grade edge computation from central reporting while using Kafka as event backbone.

## 14.1 Reference architecture (text diagram)

[Sensors/Actuators] → [DCS/PLC] → (OPC-UA) → [Gateway] → (Kafka)
                                         ├→ [GL-022 Edge Runtime] → [Write Gateway] → [DCS/PLC]
                                         └→ [Central Services: TSDB/Historian, GraphQL, Dashboards, CMMS packets]

# 15. Testing, validation, and acceptance

Testing must demonstrate control performance, deterministic correctness, and safe failure modes.

## 15.1 Test levels

Unit tests: IF97 properties, enthalpy solver, PID/anti-windup, constraints, hashing.

Integration tests: OPC-UA/Kafka ingestion, GraphQL, write gating, CMMS packet generation.

Offline replay and closed-loop simulation/HIL.

SAT: staged enabling (observe-only → advisory → supervised write → active).

# 16. Deployment, operations, and monitoring

## 16.1 Runtime requirements

Edge execution with bounded latency; monitor compute time and data freshness.

Health checks for IF97 solver convergence and write-gateway readiness.

Immutable configs per release; controlled emergency override process.

# 17. Climate intelligence and efficiency reporting

GL-022 impacts efficiency and emissions through spray usage and temperature stability. Use outputs for fuel, CO₂e, and water reporting.

## 17.1 Suggested metrics

Spray water consumption totals and intensity (kg spray per t steam).

Estimated spray duty: Q_spray ≈ m_w * (h_out - h_w_in).

Temperature stability metrics and constraint activation counts.

# 18. Appendices

## Appendix A — Tag map template

| Logical name | Tag(s) | Units | Source system | Quality rules | Notes |
| --- | --- | --- | --- | --- | --- |
| Steam outlet temperature | UNIT3.SH1.T_OUT | °C | DCS Historian | Range 0–650; ROC<5°C/s | CV for outer loop |
| Spray flow | UNIT3.ATT.MW | kg/s | Flow transmitter | Range 0–X; quality=GOOD required for active mode | Inner loop PV |
| Tube metal temp #1 | UNIT3.SH1.TMT_01 | °C | TMT system | Range 0–750; sensor status | Creep + shock |

## Appendix B — Example output record (with provenance)

{
  "ts_utc": "2026-07-15T13:05:12.345Z",
  "asset_id": "UNIT-3-SH1",
  "outputs": {
    "m_w_ff_kg_s": 2.31,
    "m_w_sp_kg_s": 2.55,
    "u_valve_cmd_pct": 37.4,
    "T_out_pred_degC": 538.0,
    "shock_risk_index": 0.62,
    "tmt_hotspot_degC": 602.3,
    "creep_damage_max": 0.18
  },
  "provenance": {
    "hash_sha256": "<computed>",
    "if97_version": "if97-1.3.0",
    "config_version": "unit3-sh1-2026-06-01",
    "software_build": "gl022-edge-2.8.4"
  }
}

## Appendix C — Glossary (selected)

| Term | Definition |
| --- | --- |
| Attemperation / Desuperheating | Injection of water into steam to reduce superheat temperature. |
| TMT | Tube Metal Temperature. |
| IF97 | IAPWS Industrial Formulation 1997 for water/steam properties. |
| Cascade control | Outer loop drives inner loop setpoint. |
| Anti-windup | Prevents PID integrator from accumulating during saturation. |
| Provenance hash | Fingerprint linking outputs to inputs/configs/software versions. |