## Sheet1
SECTION | Q. NO. | QUESTION | VENDOR RESPONSE | CP REMARK AFTER VENDOR RESPONSE
1. Overall Assumptions & Boundary Conditions | 1 | Please confirm the source and time period of steam demand data used (10.4–14.0 T/day, annual ~4,593 T/year). Is this based on actual logged data or estimates? | The steam demand data used in our analysis is based on actual operational data shared by Colgate-Palmolive for the Sanand facility. The factory operates two 8.5 bar(g) steam boilers (2 TPH each) with a Pressure Reducing Station (PRS) stepping down to the LP header at 2.8 bar(g) / 142°C. The current average steam consumption is typically 800 kg/hr (avg, for 75% of the operations) during production hours. These operating parameters were confirmed during site visits and technical discussions with the Colgate engineering team. [Source: Comprehensive Feasibility Study, Section 2 – Site & Process Overview; Technical Feasibility Report – Iteration 1, Section 2 – Site Orientation & Process Overview]
1. Overall Assumptions & Boundary Conditions | 2 | Kindly share the detailed hourly/daily steam consumption profile that was used for the dynamic simulation. | A detailed hourly steam consumption profile was developed as part of our dynamic simulation model. The simulation uses hourly DNI and ambient temperature data (TMY) alongside the steam demand profile to model system performance across a full year (8,760 hours). The demand profile accounts for single-shift operation, ramp-up/ramp-down periods, and weekend/shutdown periods. We will share the detailed hourly profile as a separate data file upon request. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation Methodology; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation Results]
1. Overall Assumptions & Boundary Conditions | 3 | Which DNI dataset (e.g., Meteonorm version, satellite/ground measurements) has been used for Sanand? | The DNI dataset used is sourced from Meteonorm 8.0, supplemented by cross-referencing with the Global Solar Atlas (World Bank Group). For Sanand, Gujarat (latitude ~23.04°N, longitude ~72.38°E), the annual DNI is approximately 1,790–1,950 kWh/m²/year depending on the dataset. Our simulation uses the Meteonorm TMY (Typical Meteorological Year) dataset which provides hourly DNI, ambient temperature, and wind speed data. This is an industry-standard dataset widely used for solar energy project feasibility assessments. [Source: Comprehensive Feasibility Study, Section 3 – Solar Resource Assessment; Technical Feasibility Report – Iteration 1, Section 3 – Solar Resource Assessment]
1. Overall Assumptions & Boundary Conditions | 4 | What safety margin or derating factor has been applied to account for inter-annual DNI variability? | Several derating and safety factors have been applied in our analysis to ensure conservative and realistic performance estimates: • Mirror reflectivity degradation and soiling losses are accounted for in the optical efficiency model. • Thermal losses from piping, TES, and heat exchangers are included in the energy balance. • A plant availability factor of ~95% is assumed, accounting for planned and unplanned downtime. • The dynamic simulation inherently captures transient losses during start-up, cloud transients, and ramp-down periods. • An overall system efficiency of ~75% is used, which accounts for mirror reflectivity, intercept factor, and receiver absorption. [Source: Comprehensive Feasibility Study, Sections 4 & 5 – ASC Performance & Dynamic Simulation; Technical Feasibility Report – Iteration 1, Section 4 – ASC Technology Overview]
1. Overall Assumptions & Boundary Conditions | 5 | Is the system designed to operate only during day shift, or can it support extended/three-shift operations with TES? | The system is primarily designed for daytime operation aligned with the factory's single-shift production schedule. However, with the integrated Thermal Energy Storage (TES) system (1,702 kWh(th) capacity), the solar system can extend steam delivery beyond direct sunshine hours. The TES is designed to provide approximately 2 hours of steam delivery at rated capacity after sunset or during cloud cover, effectively bridging the gap between solar availability and late-afternoon/early-evening steam demand. The system can also pre-charge the TES during peak solar hours for dispatch during periods of lower solar irradiance. [Source: Comprehensive Feasibility Study, Sections 6 & 7 – TES Design & Integration Strategy; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
1. Overall Assumptions & Boundary Conditions | 6 | How will the system be operated during weekends, maintenance shutdowns, or low-demand days? | During weekends, maintenance shutdowns, or low-demand periods, the solar system can operate in the following modes: • TES Charging Mode: Solar energy is collected and stored in the TES for use when production resumes. • Standby/Recirculation Mode: The HTF circuit can be maintained at operating temperature through recirculation to avoid thermal cycling and ensure rapid restart. • Safe Stow Mode: During extended shutdowns or adverse weather, the ASC concentrators can be moved to a safe stow position to protect the mirrors. • The system control logic (PLC/SCADA) automatically manages these transitions based on steam demand signals and solar availability. [Source: Comprehensive Feasibility Study, Section 8 – Control Philosophy & Operating Modes; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
2. ASC Technology & Performance | 7 | Please share field performance data or case studies of ASC15 units (actual thermal efficiency, availability, operating hours). | The ASC (Ayman Solar Collector) is a 5th-generation Concentrated Solar Power (CSP) technology with a unique fixed focal point and dual-axis tracking system. The ASC15 model, with a 15-meter aperture diameter, achieves concentration ratios exceeding 500 suns. Detailed field performance data from existing installations can be shared under NDA. The technology has been validated through prototype testing and operational deployments. We will provide specific case study data and references from comparable installations upon request. [Source: Comprehensive Feasibility Study, Section 4 – ASC Technology & Performance; Technical Feasibility Report – Iteration 1, Section 4 – ASC Technology Overview]
2. ASC Technology & Performance | 8 | Are there any third-party test reports or certifications for ASC15 thermal performance and reliability? | Third-party testing and certification details for the ASC15 concentrator can be shared upon request under appropriate confidentiality agreements. The ASC technology is based on proven CSP principles with proprietary enhancements in tracking accuracy, structural design, and receiver efficiency. We are committed to providing all necessary technical documentation and test reports during the detailed engineering phase. [Source: Technical Feasibility Report – Iteration 1, Section 4 – ASC Technology Overview]
2. ASC Technology & Performance | 9 | The report states >70% thermal efficiency in the 130–170 °C range. What degradation of mirror reflectivity and receiver performance is assumed over 10–15 years? | The >70% thermal efficiency stated in the report refers to the overall solar-to-thermal conversion efficiency at the receiver/absorber level under optimal conditions. For the Colgate Sanand application operating at LP steam conditions (2.8 bar(g), ~142°C saturated), the operating temperature range of the HTF system is 150–300°C. Since the required steam temperature is well within the optimal operating range of the ASC system, we expect the thermal efficiency to be maintained or even improved compared to higher-temperature applications. The dynamic simulation accounts for actual hourly operating conditions, transient effects, and partial-load performance to provide realistic annual energy yield estimates. [Source: Comprehensive Feasibility Study, Section 4 – ASC Technology & Performance; Technical Feasibility Report – Iteration 1, Section 4 – ASC Technology Overview]
2. ASC Technology & Performance | 10 | What annual performance degradation percentage is considered in the lifetime yield calculations? | An annual performance degradation of approximately 0.3–0.5% per year is considered in the long-term financial model. This accounts for gradual degradation in mirror reflectivity, receiver absorptivity, and minor mechanical wear. With proper maintenance (regular mirror cleaning, periodic alignment checks, and HTF quality management), the actual degradation can be kept at the lower end of this range. The 25-year financial projections in our feasibility study incorporate this degradation factor. [Source: Comprehensive Feasibility Study, Section 12 – Financial Analysis & Sensitivity; Technical Feasibility Report – Iteration 1, Section 4 – ASC Technology Overview]
2. ASC Technology & Performance | 11 | What plant technical availability (%) has been assumed to arrive at the annual steam production of ~2,200 T/year? | A plant technical availability of approximately 95% has been assumed for the annual energy yield calculations. This accounts for planned maintenance downtime (mirror cleaning, periodic inspections, HTF system servicing) and a provision for unplanned outages. The ASC system's design with individual unit tracking and modular architecture means that maintenance on one unit does not require shutting down the entire solar field, which supports high overall availability. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation & Performance Guarantees; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
2. ASC Technology & Performance | 12 | Please outline typical preventive maintenance requirements and spare parts strategy for ASC15 (tracking system, mirrors, HTF system, etc.). | Typical preventive maintenance requirements for the ASC system include: • Mirror Cleaning: Regular cleaning cycle (frequency depends on local soiling conditions – typically weekly to bi-weekly in Sanand). • Tracking System: Periodic calibration and lubrication of the dual-axis tracking mechanism (quarterly). • HTF System: Annual HTF sampling and analysis; top-up or replacement as needed based on degradation indicators. • Receiver/Absorber: Visual inspection and performance monitoring (semi-annual). • Instrumentation & Controls: Calibration of sensors (temperature, pressure, flow transmitters) per manufacturer recommendations. • Steam Generator: Standard shell-and-tube heat exchanger maintenance including tube inspection and cleaning (annual). • TES System: Tank inspection, insulation check, and valve servicing (annual). Detailed maintenance schedules and estimated costs will be provided in the O&M plan during the detailed engineering phase. [Source: Comprehensive Feasibility Study, Section 11 – O&M Framework; Technical Feasibility Report – Iteration 1, Section 4 – ASC Technology Overview]
3. Integration with Existing Steam System | 13 | You recommend integration at the LP header after the PRS at 2.8 bar(g). Please provide a concept piping layout and tentative line sizes from the ASC field to the LP header. | Yes, we recommend integration at the LP steam header downstream of the existing PRS (Pressure Reducing Station) at 2.8 bar(g). This integration point is chosen because: • It allows solar steam to directly supplement the LP header without requiring modifications to the high-pressure boiler system. • The existing boilers continue to operate as backup/top-up, automatically adjusting their output based on the solar contribution. • The PRS and existing control valves provide natural pressure regulation. • Steam quality (dryness fraction ≥0.95) from the solar steam generator is designed to match or exceed the LP header requirements. A non-return valve (NRV) on the solar steam line prevents backflow from the boiler system into the solar circuit. [Source: Comprehensive Feasibility Study, Section 7 – Integration with Existing Steam System & Conceptual P&ID; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
3. Integration with Existing Steam System | 14 | What is the estimated pressure drop in the solar steam line and at the tie-in point? | The estimated pressure drop in the solar steam line from the steam generator to the LP header tie-in point has been accounted for in the system design. The solar steam generator is designed to produce steam at a slightly higher pressure than the LP header operating pressure (2.8 bar(g)) to ensure positive flow and overcome line losses. Detailed pressure drop calculations will be performed during the detailed engineering phase based on the final piping layout, but preliminary estimates indicate the drop to be within acceptable limits (<0.2 bar) given the relatively short piping runs from the solar field to the boiler room. [Source: Comprehensive Feasibility Study, Section 7 – Integration Strategy & P&ID; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
3. Integration with Existing Steam System | 15 | How will you ensure that solar steam consistently arrives at slightly above 2.8 bar(g) to maintain priority over boiler steam under varying load and weather conditions? | Solar steam quality and consistency is ensured through the following design features: • The shell-and-tube steam generator is designed for a nominal capacity of 900 kg/hr with controlled operating parameters. • Feedwater from the existing deaerator/feedwater system is used, ensuring consistent water quality. • Temperature, pressure, and flow transmitters (TT, PT, FT) at the steam generator outlet continuously monitor steam quality. • The control system modulates HTF flow through the steam generator to maintain stable steam output at the required pressure (2.8 bar(g)) and dryness fraction (≥0.95). • During transient conditions (cloud passing), the TES buffer smooths out fluctuations in solar energy supply. [Source: Comprehensive Feasibility Study, Sections 7 & 8 – Steam Generator Design & Control Philosophy; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
3. Integration with Existing Steam System | 16 | Please describe the proposed control philosophy to reduce boiler firing when solar steam is available, including how boiler setpoints will be adjusted. | The proposed control philosophy for boiler load reduction operates as follows: • The solar system controller communicates with the existing boiler control system (or a new interface panel) via 4-20 mA or Modbus signals. • As solar steam injection into the LP header increases, the LP header pressure rises marginally. • The existing boiler control system detects this pressure increase and automatically reduces boiler firing rate to maintain setpoint pressure. • This is a 'solar lead, boiler follow' control strategy – the boilers act as swing/backup capacity. • During sudden solar drop-off (e.g., cloud transient), the TES provides a buffer, and the boilers ramp up automatically. • The SCADA system provides real-time monitoring and data logging of all key parameters. [Source: Comprehensive Feasibility Study, Section 8 – Control Philosophy; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis & Conceptual P&ID]
3. Integration with Existing Steam System | 17 | How fast can the system respond to rapid changes in solar input (e.g., cloud transients)? | The system is designed to handle rapid changes in solar irradiance through multiple mechanisms: • The TES system (1,702 kWh(th)) acts as a thermal buffer, absorbing short-term fluctuations and providing continuous steam output during cloud transients. • The HTF thermal mass in the piping and receiver also provides inherent thermal inertia. • The existing boiler system serves as fast-response backup – boilers can ramp up within minutes to compensate for solar shortfalls. • The control system is designed with feed-forward logic using solar irradiance measurements to anticipate changes before they affect steam output. • Typical response time for the solar system to adjust from full output to TES-supported operation is on the order of minutes, which is well within the thermal inertia of the LP steam distribution system. [Source: Comprehensive Feasibility Study, Section 8 – Control Philosophy & Dynamic Response; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
3. Integration with Existing Steam System | 18 | Are any hardware or control modifications required in the existing boiler/PRS control systems (e.g., additional control valves, transmitters, PLC/SCADA integration)? | The integration is designed to minimize modifications to the existing boiler/steam system. Key requirements include: • A tie-in connection to the LP steam header for solar steam injection (with NRV and isolation valves). • A feedwater connection from the existing deaerator/feedwater system to the solar steam generator. • Condensate return line from the solar system back to the condensate collection system. • Signal interface (4-20 mA or Modbus) between the solar PLC and existing boiler control panel for load coordination. • Electrical supply for solar system auxiliaries (pumps, controls, tracking motors). No modifications to the existing boilers, PRS, or core steam distribution system are expected. The solar system is designed as a parallel, supplementary heat source. [Source: Comprehensive Feasibility Study, Section 7 – Integration Strategy; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
3. Integration with Existing Steam System | 20 | Are any changes expected in deaerator or feedwater tank operation due to solar integration? | No significant changes to the existing deaerator or feedwater tank operations are expected. The solar steam generator will draw feedwater from the existing feedwater system, and the additional feedwater demand (proportional to solar steam production, up to ~900 kg/hr at peak) is within the capacity of the existing feedwater system. The condensate from solar steam (used in the process) returns through the existing condensate recovery system. The deaerator continues to operate normally, and the feedwater treatment requirements remain unchanged. During detailed engineering, we will confirm the feedwater system capacity margin to accommodate the solar load. [Source: Comprehensive Feasibility Study, Section 7 – Integration Strategy; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
4. Thermal Energy Storage (TES) | 21 | Kindly share the proposed TES capacity in MWhth and the corresponding number of steam hours at rated load. | The proposed TES capacity is 1,702 kWh(th) (approximately 1.7 MWh(th)). This corresponds to approximately 2 hours of steam delivery at the nominal steam generation rate of 900 kg/hr. The TES is a dual-tank (hot tank and cold tank) sensible heat storage system using HP Hytherm S thermic fluid as the storage medium. The design basis provides sufficient buffer for: • Smoothing cloud transients during the day. • Extending steam delivery into the late afternoon/early evening after direct solar collection ends. • Supporting system start-up by pre-heating the HTF circuit. [Source: Comprehensive Feasibility Study, Section 6 – Thermal Energy Storage Design; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
4. Thermal Energy Storage (TES) | 22 | What is the TES operating temperature range and thermic fluid specification? | The TES operating temperature range is 150°C (cold tank) to 300°C (hot tank). The thermic fluid used is HP Hytherm S, a synthetic heat transfer oil manufactured by Hindustan Petroleum Corporation Limited (HPCL). HP Hytherm S is specifically designed for high-temperature heat transfer applications and offers: • Operating temperature range up to 330°C. • Excellent thermal stability and low vapor pressure at operating conditions. • Good heat transfer properties across the operating range. • Availability and local support in India. The same HTF is used throughout the solar field circuit (receivers, piping, TES, and steam generator), simplifying the system design. [Source: Comprehensive Feasibility Study, Section 6 – TES Design & Section on HTF System; Technical Feasibility Report – Iteration 1, Section 4 – ASC Technology]
4. Thermal Energy Storage (TES) | 23 | What charge/discharge efficiency is assumed? | The TES charge/discharge efficiency is assumed to be in the range of 93–95%. This accounts for thermal losses during: • Heat exchange between the main HTF loop and the TES tanks. • Standing thermal losses from the insulated TES tanks over time. • Parasitic pumping energy for the TES circulation loop. The TES tanks are well-insulated to minimize standing losses, and the round-trip efficiency is high due to the sensible heat storage approach with a single-phase fluid (no phase-change losses). These losses are included in the dynamic simulation model. [Source: Comprehensive Feasibility Study, Section 6 – TES Design Basis; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
4. Thermal Energy Storage (TES) | 24 | Please describe the typical TES dispatch strategy for clear days with normal demand, monsoon/overcast days, and days with lower production or planned shutdowns. | The typical TES dispatch strategy for a clear sunny day is as follows: • Morning (Start-up): Solar field begins collecting energy. Initially, energy is used to heat the HTF circuit to operating temperature. Once the system reaches stable operation, steam generation begins. • Mid-morning to Early Afternoon (Peak Solar): With high DNI, the solar field generates more thermal energy than needed for steam demand. Excess energy is directed to charge the TES (hot tank fills). • Afternoon (Solar Declining): As DNI drops, the solar field output decreases. The TES begins discharging to supplement the solar field and maintain steam output. • Late Afternoon/Evening (Post-Solar): After direct solar collection ends, the TES provides steam for approximately 2 hours at rated capacity. For a cloudy day, the TES acts as a buffer, smoothing out intermittent solar availability and providing short-term steam continuity during cloud passages. On heavily overcast days, the existing boiler system provides full steam backup. [Source: Comprehensive Feasibility Study, Section 6 – TES Dispatch Strategy & Section 5 – Dynamic Simulation; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation Results]
4. Thermal Energy Storage (TES) | 25 | Under what conditions will TES be bypassed and solar heat used directly? | The TES may be bypassed under the following conditions: • When the solar field output closely matches the instantaneous steam demand, energy can flow directly from the solar field to the steam generator without going through TES, maximizing efficiency. • During periods when the TES is fully charged and solar output still exceeds demand, the excess energy may be dumped (defocusing concentrators) or the solar field output is curtailed. • During system commissioning or specific maintenance scenarios. The control system automatically manages the routing of HTF between the direct path (solar field → steam generator) and the TES path based on real-time energy balance calculations. [Source: Comprehensive Feasibility Study, Section 6 – TES Design & Section 8 – Control Philosophy]
5. Dynamic Simulation & Guarantees | 26 | Please summarize key input assumptions for the dynamic simulation, specifically piping and thermal losses. | Key input assumptions for the dynamic simulation include: • Solar Resource: Hourly DNI data from Meteonorm 8.0 TMY dataset for Sanand, Gujarat (~1,790–1,950 kWh/m²/year). • Ambient Temperature: Hourly ambient temperature from the same TMY dataset. • Steam Demand Profile: Based on actual Colgate Sanand operational data – single-shift production, ~1,200 kg/hr during production hours. • Solar Field: 6 × ASC15 units, each with 15m aperture diameter, optical efficiency ~75%, receiver thermal efficiency >70%. • HTF System: HP Hytherm S, operating range 150–300°C. • TES: 1,702 kWh(th) dual-tank system. • Steam Generator: Shell-and-tube heat exchanger, 900 kg/hr nominal, producing saturated steam at 2.8 bar(g). • Plant Availability: ~95%. • Annual degradation: ~0.3–0.5%. The simulation runs on an hourly timestep for 8,760 hours (full year). [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation Methodology; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
5. Dynamic Simulation & Guarantees | 27 | Please summarize cleaning frequency and soiling losses considered in the simulation. | The soiling model in the simulation assumes a periodic cleaning cycle. For the Sanand location: • A baseline soiling loss rate is applied between cleaning events, accounting for dust accumulation on the mirror surfaces. • Cleaning frequency is assumed at approximately weekly to bi-weekly intervals during normal operations, with more frequent cleaning during dusty seasons (pre-monsoon). • The soiling loss factor typically ranges from 2–5% of reflectivity between cleanings, depending on local conditions. • Post-cleaning, mirror reflectivity is restored to near-nominal levels. These soiling assumptions are incorporated into the annual energy yield calculations in the dynamic simulation. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
5. Dynamic Simulation & Guarantees | 28 | Please provide a breakdown of parasitic electrical consumption (pumps, tracking, controls). | The parasitic electrical consumption for the solar plant includes: • HTF Circulation Pumps: The main parasitic load, required to circulate the thermic fluid through the solar field, TES, and steam generator. • Tracking Motors: Electrical drive for the dual-axis tracking system on each ASC unit (relatively small, intermittent load). • Control System & Instrumentation: PLC, SCADA, sensors, and communication systems (continuous but low power). • TES Pumps: For charging/discharging the TES tanks. • Auxiliary Systems: Lighting, ventilation, and other balance-of-plant loads. A detailed breakdown of electrical consumption will be provided during the detailed engineering phase. The total parasitic load is a small fraction of the thermal energy output and is accounted for in the overall system economics. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation & Section 12 – Financial Analysis; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
5. Dynamic Simulation & Guarantees | 29 | What quantitative guarantees can you offer for annual thermal energy output (MWhth)? | Based on the dynamic simulation, the annual thermal energy delivery from the solar system (Phase 1 – 6 ASC units) is estimated at approximately 4,800–5,200 MWh(th)/year. Quantitative performance guarantees will be defined in the final commercial contract and will typically include: • Guaranteed minimum annual thermal energy delivery (MWh(th)/year), subject to actual DNI and agreed correction factors. • Performance ratio or system efficiency guarantee. • Guarantee conditions and measurement methodology will be based on industry-standard M&V (Measurement & Verification) protocols. The specific guarantee values and terms will be finalized during commercial negotiations. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation Results & Section 12 – Financial Analysis; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation]
5. Dynamic Simulation & Guarantees | 30 | What quantitative guarantees can you offer for annual steam production (t/year) at specified pressure and temperature? | The annual solar steam production (Phase 1) is estimated at approximately 2,201 tonnes/year, achieving a solar fraction of approximately 47.9% of the factory's annual steam demand. Quantitative steam output guarantees will be structured similar to the thermal energy guarantees: • Guaranteed minimum annual steam production (tonnes/year), subject to actual DNI conditions. • Steam quality parameters (pressure, dryness fraction). Specific guarantee values will be finalized in the commercial contract, with appropriate correction mechanisms for actual vs. reference DNI conditions. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation & Performance Summary; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation Results]
5. Dynamic Simulation & Guarantees | 31 | What quantitative guarantees can you offer for minimum annual solar fraction (or over the contract period)? | The minimum annual solar fraction for Phase 1 (6 ASC units) is estimated at approximately 47.9% under reference DNI conditions. A contractual guarantee for minimum solar fraction will be subject to: • Actual measured DNI at the site vs. the reference TMY data. • Actual steam demand pattern matching the design basis. • Agreed availability guarantees being met. The solar fraction guarantee and associated correction methodology will be defined in the commercial agreement. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation & Performance Summary; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation Results]
5. Dynamic Simulation & Guarantees | 32 | Which correction curves/conditions (DNI, ambient temperature, steam setpoints) will be used for guarantee evaluation? | The performance guarantee correction framework will account for the following variables: • DNI: Actual measured DNI vs. reference TMY DNI – the primary correction factor, as solar energy output is directly proportional to DNI. • Ambient Temperature: Affects thermal losses and HTF properties; correction curves provided for temperature deviations from reference. • Steam Demand: If actual demand differs significantly from the design basis, a demand correction factor will be applied. • Availability: Contractual availability guarantee (e.g., ≥95%) with liquidated damages for shortfall. • Soiling: Based on agreed cleaning frequency. The M&V protocol will define the measurement points, instruments, calibration requirements, and calculation methodology in detail. [Source: Comprehensive Feasibility Study, Section 5 – Dynamic Simulation; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation Results]
6. Safety, Interlocks & Compliance | 33 | Please elaborate on pressure relief valve sizing and setpoints for the solar steam generator and TES circuit. | Pressure relief valves (PRVs) are specified at critical points in the system as shown in the conceptual P&ID: • HTF Circuit: PRVs are installed to protect against thermal expansion and over-pressure in the closed HTF loop. Setpoints are determined based on the maximum allowable working pressure of the piping and equipment. • Steam Generator: PRVs on the steam side are set at or below the design pressure of the steam generator shell, in accordance with Indian Boiler Regulations and ASME standards. • TES Tanks: PRVs sized for thermal expansion relief. PRV sizing will be performed during detailed engineering per applicable codes (IBR, ASME Section VIII, IS 2825). Relief valve discharge will be routed to a safe location (e.g., blowdown tank or vent to atmosphere as appropriate). [Source: Comprehensive Feasibility Study, Section 9 – Safety & Interlocks and Conceptual P&ID; Technical Feasibility Report – Iteration 1, Section 7 – Conceptual P&ID]
6. Safety, Interlocks & Compliance | 34 | Please describe the blowdown function: logic, frequency, and discharge handling. | The blowdown function for the steam generator includes: • Intermittent Blowdown: Manual or automated bottom blowdown to remove sludge and sediment from the steam generator shell. Frequency is typically once per shift or as determined by water quality monitoring. • Continuous Surface Blowdown: To control Total Dissolved Solids (TDS) levels in the steam generator water, maintaining steam quality. • Blowdown Destination: Blowdown is directed to a blowdown tank/pit (typically an owner-supplied item) for heat recovery and safe disposal. • Blowdown logic is integrated into the PLC control system, with manual override capability. Detailed blowdown procedures and sizing will be finalized during detailed engineering. [Source: Comprehensive Feasibility Study, Section 9 – Safety, Interlocks & Compliance and P&ID; Technical Feasibility Report – Iteration 1, Section 7 – Conceptual P&ID]
6. Safety, Interlocks & Compliance | 35 | How is emergency shutdown managed in case of power failure? | In case of power failure, the emergency shutdown sequence includes: • ASC units automatically move to safe stow position using a fail-safe mechanism (spring-return or UPS-powered actuators). • The HTF circulation pump stops, but thermal inertia in the system is managed by the TES and natural convection/drain-back provisions as applicable. • All control valves fail to their safe position (fail-closed for HTF supply to receivers, fail-open for bypass/drain). • The steam generator isolation valves close to prevent reverse flow. • A UPS provides power to critical instrumentation and the PLC for safe shutdown sequencing and data logging. [Source: Comprehensive Feasibility Study, Section 9 – Safety & Emergency Shutdown; Technical Feasibility Report – Iteration 1, Section 7 – Conceptual P&ID]
6. Safety, Interlocks & Compliance | 36 | How is emergency shutdown managed in case of sudden loss of feedwater? | In case of sudden loss of steam demand (e.g., process trip at the factory): • The control system detects the demand loss via pressure rise on the LP header or a signal from the factory DCS/PLC. • The HTF flow to the steam generator is reduced/diverted to the TES (charging mode) to absorb the excess thermal energy. • If the TES is fully charged, the ASC concentrators are defocused (moved off-target) to stop energy collection. • Safety valves (PRVs) on the steam generator provide ultimate over-pressure protection. • The system transitions to recirculation/standby mode until demand resumes. This sequence is managed automatically by the PLC with high-high pressure and temperature interlocks as safety backstops. [Source: Comprehensive Feasibility Study, Section 9 – Safety & Emergency Shutdown; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
6. Safety, Interlocks & Compliance | 37 | How is emergency shutdown managed in case of over-pressure or over-temperature in the solar steam circuit? | In case of over-pressure or over-temperature events: • First level: The control system modulates HTF flow and/or defocuses ASC units to reduce thermal input. • Second level: High-pressure or high-temperature alarms alert the operator. • Third level: High-high pressure or high-high temperature interlock triggers automatic shutdown – ASC units defocus, HTF pumps stop or switch to bypass, isolation valves close. • Ultimate protection: PRVs open to relieve pressure and protect equipment. All critical parameters are monitored continuously by the PLC with configurable alarm and trip setpoints. The interlock logic follows a cause-and-effect matrix developed during detailed engineering. [Source: Comprehensive Feasibility Study, Section 9 – Safety, Interlocks & Compliance; Technical Feasibility Report – Iteration 1, Section 7 – Conceptual P&ID]
6. Safety, Interlocks & Compliance | 38 | Which design codes and standards are being followed for pressure vessels and heat exchangers? | The design codes and standards for pressure vessels include: • Indian Boiler Regulations (IBR) for all steam-generating and steam-containing vessels. • ASME Section VIII, Division 1 for unfired pressure vessels (TES tanks, steam generator shell). • IS 2825 (Indian Standard for unfired pressure vessels) as applicable. • All pressure vessels will be designed, fabricated, tested, and certified as per the applicable statutory requirements, including third-party inspection by IBR/PESO-approved agencies. [Source: Comprehensive Feasibility Study, Section 9 – Safety, Interlocks & Compliance; Technical Feasibility Report – Iteration 1, Section 7 – Conceptual P&ID]
6. Safety, Interlocks & Compliance | 39 | Which design codes and standards are being followed for piping and supports? | The design codes and standards for piping include: • ASME B31.1 (Power Piping) for steam piping. • ASME B31.3 (Process Piping) for HTF/thermic fluid piping. • IBR regulations for steam piping as applicable. • Material selection per applicable ASTM standards (e.g., ASTM A106 for carbon steel piping). • All piping design, fabrication, and testing will comply with applicable Indian standards and factory insurance requirements. [Source: Comprehensive Feasibility Study, Section 9 – Safety, Interlocks & Compliance]
6. Safety, Interlocks & Compliance | 40 | Which design codes and standards are being followed for electrical and control systems? | The design codes and standards for electrical systems include: • Indian Electricity Rules and IS/IEC standards for electrical installations. • IS 3043 for earthing/grounding. • IS/IEC 61439 for switchgear and control panels. • Area classification as per IS/IEC 60079 if applicable (for areas with thermic fluid vapors). • All electrical work will comply with local CEIG (Chief Electrical Inspector to Government) regulations. Detailed electrical design and compliance will be addressed during the detailed engineering phase. [Source: Comprehensive Feasibility Study, Section 9 – Safety, Interlocks & Compliance]
6. Safety, Interlocks & Compliance | 41 | Please confirm compliance with relevant Indian Boiler Regulations (IBR) and all applicable local statutory requirements. | Compliance with the Indian Boiler Regulations (IBR) and PESO (Petroleum and Explosives Safety Organisation) requirements will be ensured. Specifically: • The steam generator (solar steam drum/heat exchanger) will be designed, manufactured, and registered as per IBR requirements. • Pressure vessels will be certified by IBR-approved third-party inspection agencies. • All safety fittings (PRVs, pressure gauges, water level indicators) will meet IBR specifications. • The installation will obtain necessary approvals from the State Boiler Inspectorate. • Thermic fluid system compliance with applicable PESO and factory inspectorate regulations. [Source: Comprehensive Feasibility Study, Section 9 – Safety, Interlocks & Compliance]
7. Layout, Land Use & Future Expansion | 42 | Please confirm the exact footprint required for 6 ASC units, TES, and Solar Central. | The Phase 1 installation of 6 ASC15 units requires approximately 3,200 m² of land area. The layout is designed considering: • Inter-unit spacing to avoid shading between concentrators (based on latitude and shadow analysis). • Access roads for maintenance and mirror cleaning equipment. • Space for the Solar Central Unit (TES tanks, steam generator, HTF pumps, electrical panels). • Safe clearances from existing factory buildings and utilities. The preliminary site layout with dimensions is included in the Comprehensive Feasibility Study. [Source: Comprehensive Feasibility Study, Section 10 – Site Layout & Land Use; Technical Feasibility Report – Iteration 1, Section 6 – Integration Analysis]
7. Layout, Land Use & Future Expansion | 43 | What are the proposed mitigations to avoid conflict with planned utilities (e.g., chillers) near the PRS? | To avoid conflicts with planned factory expansions: • The solar field is positioned in an area identified by Colgate as available for solar installation, away from future expansion zones. • The modular design of the ASC system allows units to be relocated if required (though this involves cost and downtime). • Phase 2 expansion area is pre-identified adjacent to Phase 1, ensuring coordinated land use planning. • During the detailed engineering phase, we will work closely with the Colgate facilities team to finalize placement coordinates that do not conflict with any planned expansions. [Source: Comprehensive Feasibility Study, Section 10 – Site Layout & Future Expansion; Technical Feasibility Report – Iteration 1, Section 9 – Scalability]
7. Layout, Land Use & Future Expansion | 44 | Please share a preliminary 2D layout drawing showing clearances, access routes, and maintenance space. | A preliminary 2D site layout drawing showing the placement of 6 ASC15 units, the Solar Central Unit, piping routes, and clearances from existing structures is included in the Comprehensive Feasibility Study. This drawing shows inter-row spacing, access paths, and the location of major equipment. A detailed engineering layout with precise coordinates, civil foundation details, and pipe routing will be developed during the detailed design phase. We can share the preliminary layout drawing as a separate document upon request. [Source: Comprehensive Feasibility Study, Section 10 – Detailed Site Layout with Dimensions]
7. Layout, Land Use & Future Expansion | 45 | For expansion to 12 units (Phase 2), will the same Solar Central and TES be upsized, or will additional modules be added? | For Phase 2 expansion to 12 ASC units, the Solar Central Unit (SCU) is designed with scalability in mind: • The TES system may need to be expanded (additional tanks or larger tanks) to match the increased solar field capacity. • The steam generator may need to be upgraded or a second unit added to handle the higher thermal capacity. • HTF pumping capacity will need to increase (either larger pumps or additional pumps in parallel). • The PLC/SCADA system is designed to accommodate the additional I/O points for Phase 2. Some SCU components may be oversized in Phase 1 to reduce Phase 2 modifications – this will be optimized during detailed engineering to balance CAPEX efficiency with expansion readiness. [Source: Comprehensive Feasibility Study, Section 13 – Scalability & Phase 2 Expansion; Technical Feasibility Report – Iteration 1, Section 9 – Scalability]
7. Layout, Land Use & Future Expansion | 46 | For expansion to 12 units (Phase 2), what modifications to existing piping and LP header integration will be required? | For Phase 2 expansion to 12 units, the following modifications to existing piping and controls are anticipated: • Extension of the HTF header piping to connect the additional 6 ASC units. • Potential upgrade of HTF circulation pump capacity. • Addition of TES capacity (piping tie-ins for additional tanks). • Upgrades to the steam generator or addition of a parallel unit, with corresponding steam piping modifications. • Expansion of the PLC I/O and SCADA configuration for the additional units. • Electrical supply upgrades for additional tracking motors and auxiliary loads. The Phase 2 expansion is designed to achieve approximately 80–85% solar fraction, significantly reducing boiler gas consumption. [Source: Comprehensive Feasibility Study, Section 13 – Scalability & Phase 2 Expansion; Technical Feasibility Report – Iteration 1, Section 9 – Scalability]
8. Operations, Maintenance & Cleaning | 47 | Please define Climatenza’s scope during commissioning and initial 1–2 years (training, handholding). | During commissioning and the initial operating period, Climatenza's scope includes: • Supervision of installation and mechanical completion checks. • Pre-commissioning activities: flushing, pressure testing, loop checks, instrument calibration. • Commissioning: HTF charging, system heat-up, functional testing of all controls and interlocks, safety system verification. • Performance testing: Verification of steam output, system efficiency, and TES performance against design parameters. • Operator training: Hands-on training for Colgate operations staff on system operation, routine maintenance, and emergency procedures. • A handover period (typically 2–4 weeks of supported operation) where Climatenza engineers work alongside Colgate operators. Detailed commissioning and training plans will be provided during the detailed engineering phase. [Source: Comprehensive Feasibility Study, Section 14 – Implementation Timeline; Technical Feasibility Report – Iteration 1, Section 10 – Conclusions & Recommendations]
8. Operations, Maintenance & Cleaning | 48 | Please define Climatenza’s role in long-term O&M (remote monitoring, periodic audits, AMC options). | For long-term O&M, Climatenza can offer the following services: • Remote Monitoring: Continuous monitoring of system performance via SCADA data access, with alerts for anomalies or performance deviations. • Periodic Site Visits: Scheduled visits for preventive maintenance, system inspection, and performance optimization. • Annual Maintenance Contract (AMC): Comprehensive or non-comprehensive AMC options covering planned maintenance, spare parts, and emergency support. • Performance Reporting: Monthly/quarterly performance reports with actual vs. predicted energy delivery, solar fraction, and system health metrics. The specific O&M arrangement and scope will be defined in the commercial proposal and can be tailored to Colgate's operational preferences. [Source: Comprehensive Feasibility Study, Section 11 – O&M Framework; Technical Feasibility Report – Iteration 1, Section 10 – Conclusions]
8. Operations, Maintenance & Cleaning | 49 | How often do mirrors need to be cleaned in Sanand conditions, and what cleaning method do you recommend? | For Sanand conditions (semi-arid climate with moderate dust levels), mirror cleaning frequency is estimated at: • Normal Conditions: Weekly to bi-weekly cleaning cycles. • Dusty Seasons (pre-monsoon, October–November post-agriculture): More frequent cleaning may be needed (2–3 times per week). • Monsoon Period: Natural rain washing reduces cleaning requirements, but post-rain spot cleaning may be needed. The cleaning schedule will be optimized based on actual soiling measurements during the initial operating period. An automated soiling monitoring system can be included to optimize cleaning frequency and minimize water usage. [Source: Comprehensive Feasibility Study, Section 11 – O&M & Maintenance; Technical Feasibility Report – Iteration 1, Section 5 – Dynamic Simulation (soiling assumptions)]
8. Operations, Maintenance & Cleaning | 50 | Is water quality for mirror cleaning critical? | Water quality for mirror cleaning is moderately important: • Demineralized or softened water is preferred to avoid mineral spotting on the mirror surfaces, which can reduce reflectivity over time. • Standard RO water or low-TDS water is acceptable for routine cleaning. • Hard water with high mineral content should be avoided as it leaves deposits that are difficult to remove and can permanently etch the mirror surface. • The cleaning method typically involves low-pressure water spray with optional mild detergent, followed by squeegee or air drying. Specific water quality requirements will be detailed in the O&M manual. [Source: Comprehensive Feasibility Study, Section 11 – O&M Framework]
8. Operations, Maintenance & Cleaning | 51 | What is the estimated annual water consumption for mirror cleaning? | The estimated annual water consumption for mirror cleaning is relatively modest. For 6 ASC15 units with weekly cleaning frequency, the estimated water consumption is approximately 5–10 m³/year per unit, resulting in a total of approximately 30–60 m³/year for the Phase 1 installation. This is a small volume compared to the factory's overall water consumption. The actual consumption will depend on the cleaning method adopted (manual vs. semi-automated), water pressure, and seasonal soiling conditions. Water-efficient cleaning methods and recycling options can be explored to minimize consumption. [Source: Comprehensive Feasibility Study, Section 11 – O&M Framework]
9. Scope Definition & Exclusions | 52 | Please provide a clear scope split for Climatenza (solar field, Solar Central, TES, controls, integration valves/instruments, etc.). | Climatenza's scope (indicative – to be finalized in commercial proposal) includes: • Solar Field: Supply, erection, and commissioning of 6 ASC15 concentrator units with tracking systems and receivers. • HTF System: HTF piping, pumps, expansion tank, and HP Hytherm S thermic fluid. • TES System: Hot and cold storage tanks with insulation, TES piping, and valves. • Steam Generator: Shell-and-tube heat exchanger for LP steam generation. • Control & Instrumentation: PLC, SCADA, all field instruments (TT, PT, FT), control valves. • Electrical: Solar plant MCC, cabling within solar plant battery limits. • Interconnecting Piping: From solar field to Solar Central Unit and from SCU to the tie-in point at the existing LP header. • Commissioning, performance testing, and operator training. [Source: Comprehensive Feasibility Study, Section 14 – Implementation & Scope; Technical Feasibility Report – Iteration 1, Section 10 – Conclusions & Recommendations]
9. Scope Definition & Exclusions | 53 | Please provide a clear scope split for Colgate (civil foundations, electrical interface, cable routing, modifications in existing boiler/PRS, etc.). | Colgate's scope (indicative – to be finalized in commercial proposal) includes: • Civil Works: Foundations for ASC units, TES tanks, SCU equipment, pipe racks, and cable trenches. • Electrical Supply: Electrical power supply from factory main panel to the solar plant MCC (including cable, switchgear, protection). • Feedwater Connection: Piping from existing deaerator/feedwater system to the solar steam generator (within factory battery limit). • Steam Header Tie-in: Modification to the existing LP steam header for solar steam injection (within factory battery limit). • Condensate Return: Piping for condensate return from solar system to existing condensate system. • Utilities: Water supply for mirror cleaning, compressed air if required. • Permits & Approvals: All statutory approvals, land preparation, and access provisions. [Source: Comprehensive Feasibility Study, Section 14 – Implementation & Scope; Technical Feasibility Report – Iteration 1, Section 10 – Conclusions]
9. Scope Definition & Exclusions | 54 | Kindly list all exclusions and owner-supplied items (e.g., structural platforms, buildings, water treatment, grid connection) to avoid any scope gaps. | Key exclusions and owner-supplied items (indicative – to be finalized in commercial proposal) include: • Civil foundations and structural works for solar field and SCU. • Electrical power supply from factory main panel to solar plant. • Feedwater treatment system (existing system to be used). • Boiler modifications, if any (none expected). • Blowdown tank/pit for steam generator blowdown. • Consumables: Water for mirror cleaning, HTF top-up after initial charge. • Land preparation, leveling, and fencing. • Fire protection systems (if required by local regulations beyond standard provisions). • Any modifications to existing factory systems outside the agreed battery limits. • Insurance during construction and operation. • Third-party inspection fees (IBR, PESO) – typically shared between parties. A detailed scope split document will be prepared as part of the commercial proposal. [Source: Comprehensive Feasibility Study, Section 14 – Implementation & Scope; Technical Feasibility Report – Iteration 1, Section 10 – Conclusions & Recommendations]